## 2026
Lithgow STP - EPL 236
Sample Point 1 - Discharge to Farmers Creek
Date Data Published:21/05/2026
Water Quality
Monitoring Frequency: | Monthly
Sampled: | 2026-04-28
Result obtained: | 2026-04-29
Pollutant | Measurement |  | Units | 90 Percentile Limit | 100 Percentile Limit | Comment
BOD | <2 | 2 | mg/L | 10 | 15
Oil & Grease | <5 | 5 | mg/L | 5 | 10
pH | 7.2 | 7.2 | pH | - | 6.5 - 8.5
TSS | <2 | 2 | mg/L | 15 | 30
Total Aluminium | 0.13 | 0.13 | mg/L | - | -
Faecal Coliforms | 2 | 2 | CFU/100ml | 200 | 600
Total N | 3.16 | 3.16 | mg/L | 10 | 15
Total P | 0.058 | 0.058 | mg/L | 0.5 | 1
Ammonia | 0.28 | 0.28 | mg/L | 2 | 5
Daily Flows
Monitoring Frequency: | Daily
Readings: | 31
| Measurement |  | Units | 90 Percentile Limit | 100 Percentile Limit | Comment
Minimum | 2429 |  | KL | - | -
Maximum | 3284 |  |  | - | 10
Mean | 2779.3667 |  |  | - | -
Median | 2698.5 |  |  | - | -
Lithgow Sewerage Treatment Plant
| Summary of results for: |  |  | 2026-03-01
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2026-03-12
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
|  | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 2026-03-24 | pH | 7.2 |  | 6.5 - 8.5 | pH | No
Result obtained | 2026-03-25 | TSS | <2 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.14 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 91 | 200 | 600 | CFU/100ml | No
|  | Total N | 1.47 | 10 | 15 | mg/L | No
|  | Total P | 0.057 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.29 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| 2026-01-01 | kL
| Data | 31
| Minimum | 3076
| Maximum | 18698**
| Mean | 4820
| Median | 4136
*heavy rainfall event leading to maximum discharge
Lithgow Sewerage Treatment Plant
| Summary of results for: |  |  | 2026-02-01
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2026-03-12
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
|  | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 2026-02-24 | pH | 7.3 |  | 6.5 - 8.5 | pH | No
Result obtained | 2026-02-25 | TSS | <2 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.13 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.82 | 10 | 15 | mg/L | No
|  | Total P | 0.056 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.35 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| 2026-01-01 | kL
| Data | 31
| Minimum | 2100
| Maximum | 13770**
| Mean | 3688
| Median | 2801
*heavy rainfall event leading to maximum discharge
| Summary of results for: |  |  | 2026-01-01
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2026-03-12
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
|  | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 2026-01-27 | pH | 7.4 |  | 6.5 - 8.5 | pH | No
Result obtained | 2026-01-28 | TSS | <2 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.12 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.06 | 10 | 15 | mg/L | No
|  | Total P | 0.063 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.34 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| 2026-01-01 | kL
| Data | 31
| Minimum | 2195
| Maximum | 4516
| Mean | 2686
| Median | 2532

## 2025
| Summary of results for: |  |  | november
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2026-12-04
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
|  | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 25/11/25 | pH | 7.3 |  | 6.5 - 8.5 | pH | No
Result obtained | 26/11/25 | TSS | <2 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.17 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 1.81 | 10 | 15 | mg/L | No
|  | Total P | 0.089 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.41 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 30
| Minimum | 2526
| Maximum | 5028
| Mean | 3031
| Median | 2875
| Summary of results for: |  |  | August
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2025-03-09
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
|  | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 26/8/25 | pH | 7.2 |  | 6.5 - 8.5 | pH | No
Result obtained | 27/8/25 | TSS | 3 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.21 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 6 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.29 | 10 | 15 | mg/L | No
|  | Total P | 0.171 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.26 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 31
| Minimum | 4486
| Maximum | 17205
| Mean | 6904
| Median | 6587
| Summary of results for: |  |  | July
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2025-06-08
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
|  | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 29/7/2025 | pH | 7.2 |  | 6.5 - 8.5 | pH | No
Result obtained | 30/7/2025 | TSS | 5 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.19 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.94 | 10 | 15 | mg/L | No
|  | Total P | 0.241 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.36 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 31
| Minimum | 3417
| Maximum | 8622
| Mean | 4500
| Median | 4211
| Summary of results for: |  |  | June
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2025-02-07
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | 4 | 10 | 15 | mg/L | No
|  | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 24/6/2025 | pH | 7 |  | 6.5 - 8.5 | pH | No
Result obtained | 25/6/2025 | TSS | 19 | 15 | 30 | mg/L | Yes
|  | Total Aluminium | 0.86 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 54 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.92 | 10 | 15 | mg/L | No
|  | Total P | 0.557 | 0.5 | 1 | mg/L | Yes
|  | Ammonia | 0.55 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 30
| Minimum | 3399
| Maximum | 5255
| Mean | 4011
| Median | 3869
| Summary of results for: |  |  | May
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2025-04-06
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
|  | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 27/5/2025 | pH | 7.2 |  | 6.5 - 8.5 | pH | No
Result obtained | 28/5/25 | TSS | 3 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.23 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.44 | 10 | 15 | mg/L | No
|  | Total P | 0.129 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.22 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 31
| Minimum | 2645
| Maximum | 13529
| Mean | 4748
| Median | 3195 | [5 empty] | *missing data due to outflow meter issue
| Summary of results for: |  |  | April
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2025-07-05
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
| 2025-02-26 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 29/4/2025 | pH | 7.2 |  | 6.5 - 8.5 | pH | No
Result obtained | 30/4/25 | TSS | 3 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.3 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 3 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.15 | 10 | 15 | mg/L | No
|  | Total P | 0.189 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.46 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 30
| Minimum | 2251
| Maximum | 10491
| Mean | 3204
| Median | 2706 | [5 empty] | *missing data due to outflow meter issue
| Summary of results for: |  |  | March
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2025-04-03
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
|  | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 2025-03-05 | pH | 7.4 |  | 6.5 - 8.5 | pH | No
Result obtained |  | TSS | 4 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.16 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.39 | 10 | 15 | mg/L | No
|  | Total P | 0.116 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.32 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 27
| Minimum | 2079
| Maximum | 7006
| Mean | 3162
| Median | 2877 | [5 empty] | *missing data due to outflow meter issue
| Summary of results for: |  |  | February
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2025-03-07
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
|  | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 2025-03-05 | pH | 7.3 |  | 6.5 - 8.5 | pH | No
Result obtained |  | TSS | 6 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.27 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.87 | 10 | 15 | mg/L | No
|  | Total P | 0.151 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.47 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 28
| Minimum | 2437
| Maximum | 9579
| Mean | 3682
| Median | 3018
| Summary of results for: |  |  | January
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2025-05-02
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
|  | Oil & Grease | <5 | 5 | 10 | mg/L | No
Sampled | 2025-01-29 | pH | 7.6 |  | 6.5 - 8.5 | pH | No
Result obtained | 2025-05-02 | TSS | <2 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.17 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.79 | 10 | 15 | mg/L | No
|  | Total P | 0.118 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.2 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 31
| Minimum | 2091
| Maximum | 6526
| Mean | 3594
| Median | 3316

## 2024
| Summary of results for: |  |  | December
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2025-01-09
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
Sampled | 2024-11-17 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained | 2024-12-31 | pH | 7.5 |  | 6.5 - 8.5 | pH | No
|  | TSS | <2 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.27 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.15 | 10 | 15 | mg/L | No
|  | Total P | 0.067 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.28 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 31
| Minimum | 2505
| Maximum | 12851
| Mean | 4809
| Median | 3498
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Summary of results for: |  |  | November
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2024-12-06
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
Sampled | 2024-11-26 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained | 2024-12-06 | pH | 7.5 |  | 6.5 - 8.5 | pH | No
|  | TSS | <2 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.21 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 5 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.48 | 10 | 15 | mg/L | No
|  | Total P | 0.091 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.4 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 30
| Minimum | 2421
| Maximum | 7803
| Mean | 3012
| Median | 2602
| Summary of results for: |  |  | October
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2024-11-08
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
Sampled | 2024-10-29 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained | 2024-11-06 | pH | 7.3 |  | 6.5 - 8.5 | pH | No
|  | TSS | <2 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.34 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 5 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.2 | 10 | 15 | mg/L | No
|  | Total P | 0.092 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.37 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 31
| Minimum | 2615
| Maximum | 5525
| Mean | 3167
| Median | 2970
| Summary of results for: |  |  | September
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2024-10-08
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
Sampled | 2024-09-24 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained | 2024-10-03 | pH | 7.4 |  | 6.5 - 8.5 | pH | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.36 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 3 | 200 | 600 | CFU/100ml | No
|  | Total N | 1.97 | 10 | 15 | mg/L | No
|  | Total P | 0.11 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.36 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| September | kL
| Data | 31
| Minimum | 2701
| Maximum | 6579
| Mean | 3197
| Median | 2930
| Summary of results for: |  |  | August
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2024-09-12
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
Sampled | 2024-08-27 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained | 2024-09-10 | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS | <2 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.26 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.15 | 10 | 15 | mg/L | No
|  | Total P | 0.086 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.2 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| February | kL
| Data | 31
| Minimum | 2589
| Maximum | 6430
| Mean | 3918
| Median | 3808
| Summary of results for: |  |  | July
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2024-08-19
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
Sampled | 2024-07-30 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained | 2024-08-19 | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.23 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.73 | 10 | 15 | mg/L | No
|  | Total P | 0.108 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.1 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| February | kL
| Data | 31
| Minimum | 3977
| Maximum | 7940
| Mean | 5262
| Median | 4824
| Summary of results for: |  |  | June
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2024-07-09
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
Sampled | 2024-06-25 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained | 2024-07-04 | pH | 7 |  | 6.5 - 8.5 | pH | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.31 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 6.03 | 10 | 15 | mg/L | No
|  | Total P | 0.141 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.15 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| February | kL
| Data | 30
| Minimum | 4026
| Maximum | 14113**
| Mean | 6564
| Median | 5888
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Summary of results for: |  |  | May
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
| Date Data Published: |  |  | 2024-07-09
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
Sampled | 2024-05-28 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained | 2024-06-08 | pH | 7 |  | 6.5 - 8.5 | pH | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.26 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.85 | 10 | 15 | mg/L | No
|  | Total P | 0.102 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.2 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| February | kL
| Data | 31
| Minimum | 3563
| Maximum | 14,534**
| Mean | 5988
| Median | 4965
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Summary of results for: |  |  | April
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Results Submitted | 2024-05-28 | BOD | <2 | 10 | 15 | mg/L | No
Sampled | 2024-04-23 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained | 2024-05-03 | pH | 7.3 |  | 6.5 - 8.5 | pH | No
|  | TSS | 5 | 15 | 30 | mg/L | Yes
|  | Total Aluminium | 0.38 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 6.62 | 10 | 15 | mg/L | No
|  | Total P | 0.109 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.17 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| February | kL
| Data | 30
| Minimum | 2323
| Maximum | 24,119**
| Mean | 5876
| Median | 4162
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Summary of results for: |  |  | March
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | 2 | 10 | 15 | mg/L | No
Sampled | 2024-03-26 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained | 2024-04-05 | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS | 15 | 15 | 30 | mg/L | Yes | 90 percentile exceedance(due to decant repairs)
|  | Total Aluminium | 1.01 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 9 | 200 | 600 | CFU/100ml | No
|  | Total N | 11 | 10 | 15 | mg/L | No
|  | Total P | 0.476 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.78 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| February | kL
| Data | 31
| Minimum | 2601
| Maximum | 5417
| Mean | 3134
| Median | 2996
| Summary of results for: |  |  | February
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
|  | BOD | <2 | 10 | 15 | mg/L | No
Sampled | 2024-02-27 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained | 2024-03-11 | pH | 7.4 |  | 6.5 - 8.5 | pH | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.37 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.72 | 10 | 15 | mg/L | No
|  | Total P | 0.167 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.4 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| February | kL
| Data | 29
| Minimum | 2899
| Maximum | 11714**
| Mean | 3918
| Median | 3703
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Summary of results for: |  |  | January
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
| 2024-01-30 | BOD | <2 | 10 | 15 | mg/L | No
Sampled | 2024-02-07 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained |  | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS | 10 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.78 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 2 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.29 | 10 | 15 | mg/L | No
|  | Total P | 0.297 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.31 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 31
| Minimum | 3826
| Maximum | 19690**
| Mean | 7712
| Median | 6027
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.

## 2023
| Lithgow Sewerage Treatment Plant |  |  | 45093
| Date Data Published: |  |  | 2023-12-19
| Summary of results for: |  |  | December
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  | EPL no. 236
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Comment
Sampled | 2023-09-26 | BOD | 2 | 10 | 15 | mg/L | No
Result obtained | 2023-10-04 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.3 |  | 6.5 - 8.5 | pH | No
|  | TSS | 9 | 15 | 30 | mg/L | Yes
|  | Total Aluminium | 0.62 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 2 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.37 | 10 | 15 | mg/L | No
|  | Total P | 0.305 | 0.5 | 1 | mg/L | Yes
|  | Ammonia | 0.95 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| December | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2413
| Maximum | 23078**
| Mean | 5234
| Median | 3994
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Summary of results for: |  |  | November
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
| 2023-11-28 | BOD | 3 | 10 | 15 | mg/L | No
Sampled | 2023-12-07 | Oil & Grease | <5 | 5 | 10 | mg/L | No
Result obtained |  | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS | 12 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.97 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.41 | 10 | 15 | mg/L | No
|  | Total P | 0.424 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.78 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| November | kL
| Data | 31
| Minimum | 2079
| Maximum | 16,867**
| Mean | 3712
| Median | 2599
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Lithgow Sewerage Treatment Plant |  |  | 45093
| Date Data Published: |  |  | 2023-10-26
| Summary of results for: |  |  | September
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  | EPL no. 236
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Comment
Sampled | 2023-09-26 | BOD | 6 | 10 | 15 | mg/L | No
Result obtained | 2023-10-04 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.3 |  | 6.5 - 8.5 | pH | No
|  | TSS | 15 | 15 | 30 | mg/L | Yes
|  | Total Aluminium | 0.95 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.06 | 10 | 15 | mg/L | No
|  | Total P | 0.555 | 0.5 | 1 | mg/L | Yes
|  | Ammonia | 0.54 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| September | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2306
| Maximum | 6759
| Mean | 3034
| Median | 2736
| Lithgow Sewerage Treatment Plant |  |  | 45093
| Date Data Published: |  |  | 2023-09-20
| Summary of results for: |  |  | August
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  | EPL no. 236
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Comment
Sampled | 2023-08-29 | BOD | 6 | 10 | 15 | mg/L | No
Result obtained | 2023-09-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.1 |  | 6.5 - 8.5 | pH | No
|  | TSS | 34 | 15 | 30 | mg/L | Yes | Non-compliance August 2023 due to carry over in the decant sequence producing a higher than usual Total P and TSS results, Our test results 0n that day of the 29th August were Total P 0.31 and TSS 7
|  | Total Aluminium | 2.36 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.59 | 10 | 15 | mg/L | No
|  | Total P | 1.02 | 0.5 | 1 | mg/L | Yes | Non-compliance August 2023 due to carry over in the decant sequence producing a higher than usual Total P and TSS results, Our test results 0n that day of the 29th August were Total P 0.31 and TSS 7
|  | Ammonia | 0.85 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| August | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2306
| Maximum | 6759
| Mean | 3034
| Median | 2736
| Lithgow Sewerage Treatment Plant |  |  | 45093
| Date Data Published: |  |  | 2023-08-08
| Summary of results for: |  |  | July
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  | EPL no. 236
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Comment
Sampled | 2023-07-26 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2023-08-03 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS | 14 | 15 | 30 | mg/L | No
|  | Total Aluminium | 1.16 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.61 | 10 | 15 | mg/L | No
|  | Total P | 0.475 | 0.5 | 1 | mg/L | No
|  | Ammonia | 1.39 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| June | kL |  |  |  | mg/L = milligrams per litre
| Data | 17 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2546
| Maximum | 3033
| Mean | 2725
| Median | 2679
Sample Point 3
|  | Pollutant | Measurement | Units
| 2023-07-26 | BOD | <2 | mg/L
| 2023-08-03 | Oil & Grease | <5 | mg/L
|  | pH | 7.2 | pH
|  | TSS | <2 | mg/L
|  | Total Aluminium | 0.06 | mg/L
|  | Faecal Coliforms | ~93 | cfu/100mL
|  | Total N | 0.18 | mg/L
|  | Total P | 0.002 | mg/L
|  | Ammonia | <0.01 | mg/L
Sample Point 4
|  | Pollutant | Measurement | Units
| 2023-07-26 | BOD | <2 | mg/L
| 2023-08-03 | Oil & Grease | <5 | mg/L
|  | pH | 7.4 | pH
|  | TSS | 3 | mg/L
|  | Total Aluminium | 0.2 | mg/L
|  | Faecal Coliforms | 32 | cfu/100mL
|  | Total N | 2 | mg/L
|  | Total P | 0.076 | mg/L
|  | Ammonia | 0.51 | mg/L
| Lithgow Sewerage Treatment Plant |  |  | 45093
| Date Data Published: |  |  | 2023-07-07
| Summary of results for: |  |  | June
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  | EPL no. 236
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Comment
Sampled | 2023-06-27 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2023-07-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.3 |  | 6.5 - 8.5 | pH | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.11 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.3 | 10 | 15 | mg/L | No
|  | Total P | 0.153 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.4 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| June | kL |  |  |  | mg/L = milligrams per litre
| Data | 29 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2562
| Maximum | 5298
| Mean | 2889
| Median | 2772
| Lithgow Sewerage Treatment Plant |  |  | 45093
| Date Data Published: |  |  | 2023-06-16
| Summary of results for: |  |  | May
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  | EPL no. 236
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Comment
Sampled | 2023-05-30 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2023-06-07 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.36 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 5.63 | 10 | 15 | mg/L | No
|  | Total P | 0.113 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.36 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2474
| Maximum | 5073
| Mean | 3100
| Median | 2925
| Lithgow Sewerage Treatment Plant |  |  | 45093
| Date Data Published: |  |  | 2023-04-28
| Summary of results for: |  |  | April
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Comment
Sampled | 2023-04-18 | BOD | 2 | 10 | 15 | mg/L | No
Result obtained | 2023-04-28 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS * | 22 | 15 | 30 | mg/L | No
|  | Total Aluminium | 1.59 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 10.1 | 10 | 15 | mg/L | No
|  | Total P * | 0.655 | 0.5 | 1 | mg/L | No
|  | Ammonia | 1.01 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| April | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2649
| Maximum | 17461
| Mean | 3983
| Median | 3124 | * | Total P 90 Percentile limit exceeded due to broken decant bellows
| Lithgow Sewerage Treatment Plant |  |  | 45093
| Date Data Published: |  |  | 2023-04-11
| Summary of results for: |  |  | March
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2023-03-28 | BOD | 2 | 10 | 15 | mg/L | No
Result obtained | 2023-04-05 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.1 |  | 6.5 - 8.5 | pH | No
|  | TSS * | 20 | 15 | 30 | mg/L | No
|  | Total Aluminium | 1.9 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 4 | 200 | 600 | CFU/100ml | No
|  | Total N | 7.17 | 10 | 15 | mg/L | No
|  | Total P * | 0.75 | 0.5 | 1 | mg/L | No
|  | Ammonia | 1.05 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2290
| Maximum | 6502
| Mean | 3141
| Median | 2746 | * | Total P 90 Percentile limit exceeded
| Lithgow Sewerage Treatment Plant |  |  | 45093
| Date Data Published: |  |  | 2023-03-07
| Summary of results for: |  |  | February
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2023-02-21 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2023-03-01 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.47 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 22 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.02 | 10 | 15 | mg/L | No
|  | Total P | 0.211 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.32 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| February | kL |  |  |  | mg/L = milligrams per litre
| Data | 28 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2890
| Maximum | 6753
| Mean | 3651
| Median | 3411
Lithgow Sewerage Treatment Plant
| Date Data Published: |  |  | 2023-02-02
| Summary of results for: |  |  | January
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2023-01-24 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2023-02-01 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS | 7 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.46 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 2 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.24 | 10 | 15 | mg/L | No
|  | Total P | 0.192 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.32 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| January | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 3264
| Maximum ** | 11060
| Mean | 5100 |  | **Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Median | 4591

## 2022
| Date Data Published: |  |  | 2022-01-13
| Summary of results for: |  |  | December
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2022-11-25 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2022-11-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS | 11 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.6 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 16 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.58 | 10 | 15 | mg/L | No
|  | Total P | 0.449 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.61 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 28
| Minimum | 3009
| Maximum ** | 6990
| Mean | 3978
| Median | 3831
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-01-13
| Summary of results for: |  |  | November
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2022-11-29 | BOD | 3 | 10 | 15 | mg/L | No
Result obtained | 2022-12-09 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.1 |  | 6.5 - 8.5 | pH | No
|  | TSS | 10 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.87 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.5 | 10 | 15 | mg/L | No
|  | Total P | 0.433 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.17 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 28
| Minimum | 4949
| Maximum ** | 20120
| Mean | 7877
| Median | 6457
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-11-14
| Summary of results for: |  |  | October
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2022-10-25 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2022-11-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.1 |  | 6.5 - 8.5 | pH | No
|  | TSS | 11 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.68 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 4 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.43 | 10 | 15 | mg/L | No
|  | Total P | 0.324 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.58 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 28
| Minimum | 6027
| Maximum ** | 19264
| Mean | 9060
| Median | 8261
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-10-13
| Summary of results for: |  |  | September
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2022-09-27 | BOD | 4 | 10 | 15 | mg/L | No
Result obtained | 2022-10-09 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.2 |  | 6.5 - 8.5 | pH | No
| * | TSS | 26 | 15 | 30 | mg/L | No
|  | Total Aluminium | 1.64 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 11 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.58 | 10 | 15 | mg/L | No
| * | Total P | 0.755 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.58 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 31
| Minimum | 4619
| Maximum ** | 15602
| Mean | 7067
| Median | 6228
* Note: 90 Percentile limits exceeded due to wet weather events
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-09-19
| Summary of results for: |  |  | August
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2022-08-31 | BOD | 2 | 10 | 15 | mg/L | No
Result obtained | 2022-09-09 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.1 |  | 6.5 - 8.5 | pH | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.34 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 6.62 | 10 | 15 | mg/L | No
|  | Total P | 0.144 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.25 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 31
| Minimum | 4807
| Maximum | 13914
| Mean | 6888
| Median | 6430
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-08-12
| Summary of results for: |  |  | July
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2022-07-26 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2022-08-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.1 |  | 6.5 - 8.5 | pH | No
|  | TSS | 12 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.47 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.48 | 10 | 15 | mg/L | No
|  | Total P | 0.475 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.2 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 31
| Minimum | 4261
| Maximum | 17370**
| Mean | 10123**
| Median | 8534
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-08-12
| Summary of results for: |  |  | 2021-22
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Annual
Sample Point 3
Environment Monitoring 100 metres upstream of the confluence between the discharge channel and Farmers Creek
Licensee: Lithgow City Council
|  | Pollutant | Measurement | Units
Sampled | 2022-07-26 | BOD | <2 | mg/L
Result obtained | 2022-08-06 | Oil & Grease | <5 | mg/L
|  | pH | 7 | pH
|  | TSS | 13 | mg/L
|  | Aluminium | 0.62 | mg/L
|  | Faecal Coliforms | 68 | CFU/100ml
|  | Total N | 0.41 | mg/L
|  | Total P | 0.017 | mg/L
|  | Ammonia | <0.01 | mg/L
| Date Data Published: |  |  | 2022-08-12
| Summary of results for: |  |  | 2021-22
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Annual
Sample Point 4
Environment Monitoring 200 metres upstream of the confluence between the discharge channel and Farmers Creek
Licensee: Lithgow City Council
|  | Pollutant | Measurement | Units
Sampled | 2022-07-26 | BOD | <2 | mg/L
Result obtained | 2022-08-06 | Oil & Grease | <5 | mg/L
|  | pH | 7.1 | pH
|  | TSS | 9 | mg/L
|  | Aluminium | 0.48 | mg/L
|  | Faecal coliforms | 58 | cfu/100mL
|  | Total N | 0.6 | mg/L
|  | Total P | 0.033 | mg/L
|  | Ammonia | 0.02 | mg/L
| Date Data Published: |  |  | 2022-07-15
| Summary of results for: |  |  | June
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2022-06-28 | BOD | 2 | 10 | 15 | mg/L | No
Result obtained | 2022-07-09 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.3 |  | 6.5 - 8.5 | pH | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.53 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.77 | 10 | 15 | mg/L | No
|  | Total P | 0.203 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.85 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 30
| Minimum | 2995
| Maximum | 7284
| Mean | 4681
| Median | 4561
| Date Data Published: |  |  | 2022-06-15
| Summary of results for: |  |  | May
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2022-05-24 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2022-06-03 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.1 |  | 6.5 - 8.5 | pH | No
|  | TSS | 9 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.71 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.91 | 10 | 15 | mg/L | No
|  | Total P | 0.315 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.01 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 31
| Minimum | 4859
| Maximum | 8236
| Mean | 6510
| Median | 6486
| Date Data Published: |  |  | 2022-04-11
| Summary of results for: |  |  | March
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2022-03-29 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2022-04-08 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.2 |  | 6.5 - 8.5 | pH | No
|  | TSS | 11 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.77 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 3 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.54 | 10 | 15 | mg/L | No
|  | Total P | 0.277 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.53 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 31
| Minimum | 5517
| Maximum | 23090**
| Mean | 11141**
| Median | 9170
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-03-07
| Summary of results for: |  |  | February
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2022-02-21 | BOD | 2 | 10 | 15 | mg/L | No
Result obtained | 2022-03-03 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.4 |  | 6.5 - 8.5 | pH | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.35 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 7 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.51 | 10 | 15 | mg/L | No
|  | Total P | 0.171 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.4 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 28
| Minimum | 4226
| Maximum | 10173**
| Mean | 6457.3929
| Median | 6232.5
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-02-07
| Summary of results for: |  |  | January
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedance | Comment
Sampled | 2022-01-25 | BOD | 2 | 10 | 15 | mg/L | No
Result obtained | 2022-02-03 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7 |  | 6.5 - 8.5 | pH | No
|  | TSS | 10 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.69 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 3 | 200 | 600 | CFU/100ml | No
|  | Total N | 7.06 | 10 | 15 | mg/L | No
|  | Total P | 0.265 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.24 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 31
| Minimum | 4485
| Mean | 10395**
| Median | 9744
| Maximum | 22483**
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.

## 2021
Lithgow Sewage Treatment Plant
| Date Data Published: |  |  | 2022-01-12
| Summary of results for: |  |  | December
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Comment
Sampled | 2021-12-21 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2021-12-31 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.3 |  | 6.5 - 8.5 | pH | No
|  | TSS | 11 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.79 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.17 | 10 | 15 | mg/L | No
|  | Total P | 0.355 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.26 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 31
| Minimum | 4301
| Mean | 6632.42
| Median | 6215
| Maximum | 10603
| Date Data Published: |  |  | 2021-12-09
| Summary of results for: |  |  | November
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Comment
Sampled | 2021-11-23 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2021-12-08 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.1 |  | 6.5 - 8.5 | pH | No
|  | TSS | 18 | 15 | 30 | mg/L | 90th percentile | 90th percentile exceeded for Total Suspended Solids. 100th percentile exceeded previously.
|  | Total Aluminium | 1.22 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.14 | 10 | 15 | mg/L | No
|  | Total P | 0.475 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.02 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 30
| Minimum | 2910
| Mean | 8127
| Median | 6692
| Maximum | 20493
| Date Data Published: |  |  | 2021-11-10
| Summary of results for: |  |  | October
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Comment
Sampled | 2021-10-26 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2021-11-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.4 |  | 6.5 - 8.5 | pH | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.07 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 530 | 200 | 600 | CFU/100ml | 90th percentile | 90th percentile exceeded for Ammonia. First for this reporting period.
|  | Total N | 2.27 | 10 | 15 | mg/L | No
|  | Total P | 0.237 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.71 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| October | kL
| Data | 31
| Minimum | 2966
| Mean | 3997.097
| Median | 3682
| Maximum | 7208
| Date Data Published: |  |  | 2021-10-07
| Summary of results for: |  |  | September
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Comment
Sampled | 2021-09-28 | BOD | 3 | 10 | 15 | mg/L | No
Result obtained | 2021-10-07 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.3 |  | 6.5 - 8.5 | pH | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.28 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 5.25 | 10 | 15 | mg/L | No
|  | Total P | 0.197 | 0.5 | 1 | mg/L | No
|  | Ammonia | 4.03 | 2 | 5 | mg/L | 90th percentile | 90th percentile exceeded for Ammonia. First for this reporting period.
Point 1
| Month | Volume Discharged
| September | kL
| Data | 30
| Minimum | 3179
| Mean | 4308.5
| Median | 4167.5
| Maximum | 6379
| Date Data Published: |  |  | 2021-09-13
| Summary of results for: |  |  | August
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Comment
Sampled | 2021-08-31 | BOD | <2 | 10 | 15 | mg/L | No
Result obtained | 2021-09-10 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.4 |  | 6.5 - 8.5 | pH | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Total Aluminium | 0.37 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | 2 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.02 | 10 | 15 | mg/L | No
|  | Total P | 0.1 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.28 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| August | kL
| Data | 31
| Minimum | 2913
| Mean | 4694
| Median | 3680
| Maximum | 18031
| Date Data Published: |  |  | 2021-08-10
| Summary of results for: |  |  | July
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Comment
Sampled | 2021-07-27 | BOD | 6 | 10 | 15 | mg/L | No | 100th percentile exceedance for TSS and 90th percentile exceedance for Total Nitrogen and Phosphorus. Cause to be investigated and updated here.
Result obtained | 2021-08-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7 |  | 6.5 - 8.5 | pH | No
|  | TSS | 42 | 15 | 30 | mg/L | Yes
|  | Total Aluminium | 2.38 | n/a | n/a | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 12.9 | 10 | 15 | mg/L | Yes
|  | Total P | 0.785 | 0.5 | 1 | mg/L | Yes
|  | Ammonia | 0.4 | 2 | 5 | mg/L | No
Point 1
| Month | Volume Discharged
| July | kL
| Data | 17
| Minimum | 3053
| Mean | 4226
| Median | 4276
| Maximum | 5972
| Date Data Published: |  |  | 2021-08-09
| Summary of results for: |  |  | 2020-21
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Annual
Sample Point 3
Environment Monitoring 100 metres upstream of the confluence between the discharge channel and Farmers Creek
Licensee: Lithgow City Council
|  | Pollutant | Measurement | Units
Sampled | 2021-07-27 | BOD | <2 | mg/L
Result obtained | 2021-08-06 | Oil & Grease | <5 | mg/L
|  | pH | 7.4 | pH
|  | TSS | 4 | mg/L
|  | Aluminium | 0.16 | mg/L
|  | Faecal Coliforms | 560 | CFU/100ml
|  | Total N | 0.67 | mg/L
|  | Total P | 0.008 | mg/L
|  | Ammonia | 0.04 | mg/L
| Date Data Published: |  |  | 2021-08-09
| Summary of results for: |  |  | 2020-21
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Annual
Sample Point 4
Environment Monitoring 200 metres upstream of the confluence between the discharge channel and Farmers Creek
Licensee: Lithgow City Council
|  | Pollutant | Measurement | Units
Sampled | 2021-07-27 | BOD |  | mg/L
Result obtained | 2021-08-06 | Oil & Grease |  | mg/L
|  | pH |  | pH
|  | TSS |  | mg/L
|  | Aluminium |  | cfu/100mL
|  | Faecal coliforms |  | mg/L
|  | Total N |  | mg/L
|  | Total P |  | mg/L
|  | Ammonia |  | mg/L
| Date Data Published: |  |  | 2021-07-13
| Summary of results for: |  |  | June
| Number of measurements taken: |  |  | None
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Comment
|  | BOD |  | 10 | 15 | mg/L |  | Lithgow Sewage Treatment Plant was offline for desludging works from 22nd June,2021 and therefore no measurements were taken
|  | Oil & Grease |  | 5 | 10 | mg/L
|  | pH |  |  | 6.5 - 8.5 | pH
|  | TSS |  | 15 | 30 | mg/L
|  | Faecal Coliforms |  | 200 | 600 | cfu/100mL
|  | Ammonia |  | 2 | 5 | mg/L
|  | Total P |  | 0.5 | 1 | mg/L
|  | Total N |  | 10 | 15 | mg/L
|  | Aluminium |  | n/a | n/a | mg/L
Point 1
| Month | Volume Discharged
| June | kL
| Data | 24
| Minimum | 2782
| Mean | 3635
| Median | 3463
| Maximum | 5322
| Date Data Published: |  |  | 2021-06-04
| Summary of results for: |  |  | `May
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
| Sampled 25/05/2021 | BOD | <2 | 10 | 15 | mg/L | No
| Result Obtained 03/06/2021 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.23 |  | 6.5 - 8.5 | pH | No
|  | TSS | 6 | 15 | 30 | mg/L | No
|  | Faecal Coliforms | 20 | 200 | 600 | cfu/100mL | No
|  | Ammonia | 0.5 | 2 | 5 | mg/L | No
|  | Total P | 0.247 | 0.5 | 1 | mg/L | No
|  | Total N | 2.92 | 10 | 15 | mg/L | No
|  | Aluminium | 0.45 | n/a | n/a | mg/L
| Point 1 |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  | mg/L = milligrams per litre
| Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2988
| Mean | 3976.5
| Median | 3509
| Maximum | 10138*
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2021-04-15
| Summary of results for: |  |  | March
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
| Sampled 30/03/2021 | BOD | <2 | 10 | 15 | mg/L | No
| Result Obtained 10/04/2021 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.3 |  | 6.5 - 8.5 | pH | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Faecal Coliforms | 16 | 200 | 600 | cfu/100mL | No
|  | Ammonia | 0.37 | 2 | 5 | mg/L | No
|  | Total P | 0.157 | 0.5 | 1 | mg/L | No
|  | Total N | 3.17 | 10 | 15 | mg/L | No
|  | Aluminium | 0.28 | n/a | n/a | mg/L
| Point 1 |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  | mg/L = milligrams per litre
| Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2950
| Mean | 8258.87
| Median | 5731
| Maximum | 25268**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2021-03-17
| Summary of results for: |  |  | February
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
| Sampled 23/02/2021 | BOD | <2 | 10 | 15 | mg/L | No
| Obtained 11/03/2021 | Oil & Grease | 7 | 5 | 10 | mg/L | No
|  | pH | 7.3 |  | 6.5 - 8.5 | pH | No
|  | TSS | 7 | 15 | 30 | mg/L | No
|  | Faecal Coliforms | 100 | 200 | 600 | cfu/100mL | No
|  | Ammonia | 0.37 | 2 | 5 | mg/L | No
|  | Total P | 0.179 | 0.5 | 1 | mg/L | No
|  | Total N | 1.83 | 10 | 15 | mg/L | No
|  | Aluminium | 0.58 |  |  | mg/L
| Point 1 |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| February | kL |  |  | mg/L = milligrams per litre
| Data | 28 |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 3135
| Mean | 4921
| Median | 4574
| Maximum | 10,948**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2021-02-22
| Summary of results for: |  |  | January
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
| Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
|  | Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
| Sampled 27/01/2021 | BOD | 15 | 10 | 15 | mg/L | Yes | During the months of December 2020 and January 2021, Lithgow STP suffered 2 process equipment failures, that have led to test results out of limits for the licence. The failure of a rubber bellows on IDEA Tank 2, allowed untreated effluent and sludge to pass into the catchment pond for that tank. The failure was first detected on 01/01/2021, but may have been leaking prior to that date. During the month of January, the break was monitored, whilst a specialist contractor could be arranged to replace the bellows. This was completed on 05/02/2021. The gradual failure of the bellows is believed to have contributed to the exceedances in Total Suspended Solids (TSS), Phosphorous (Total P), Ammonia (NH4) and Biological Oxygen Demand (BOD), over this period. A failure of the auto control system for the UV sterilisation plant on site, has stopped the UV sterilisation of effluent leaving the plant for a period of time. The sample provided in January, was from effluent that had not been UV sterilised. This system has now been rectified.
| Obtained 10/02/2021 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.1 |  | 6.5 - 8.5 | pH | No
|  | TSS | 18 | 15 | 30 | mg/L | Yes
|  | Faecal Coliforms | ~6800 | 200 | 600 | cfu/100mL | Yes
|  | Ammonia | 2.2 | 2 | 5 | mg/L | Yes
|  | Total P | 0.86 | 0.5 | 1 | mg/L | Yes
|  | Total N | 4.28 | 10 | 15 | mg/L | No
|  | Aluminium | 1.42 |  |  | mg/L
| Point 1 |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| January | kL |  |  | mg/L = milligrams per litre
| Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 2782
| Mean | 4968
| Median | 4125
| Maximum | 12,429**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.

## 2020
Lithgow Sewage Treatment Plant
Date Data Published: |  |  | 2021-01-18
Summary of results for: |  |  | December
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 16/12/2020 | BOD | 4 | 10 | 15 | mg/L | No
Obtained 11/01/2021 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.6 |  | 6.5 - 8.5 | pH | No
| TSS | 21 | 15 | 30 | mg/L | No
| Faecal Coliforms | ~400 | 200 | 600 | cfu/100mL | No
| Ammonia | 2.78 | 2 | 5 | mg/L | No
| Total P | 0.63 | 0.5 | 1 | mg/L | No
| Total N | 5.09 | 10 | 15 | mg/L | No
| Aluminium | 0.77 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
December | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 1810
Mean | 4554
Median | 3468
Maximum | 15,278**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-12-22
Summary of results for: |  |  | November
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 24/11/2020 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 14/12/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.6 |  | 6.5 - 8.5 | pH | No
| TSS | 18 | 15 | 30 | mg/L | No
| Faecal Coliforms | 210 | 200 | 600 | cfu/100mL | No
| Ammonia | 5.08 | 2 | 5 | mg/L | Yes | Lithgow STP had a process failure on the day prior to sampling. Effluent from the site was diverted to the storage lagoons as per the EPA licence for the site. Effluent was diverted back to the environment just prior to the sample for November being taken.
| Total P | 0.82 | 0.5 | 1 | mg/L | No
| Total N | 7.64 | 10 | 15 | mg/L | No
| Aluminium | 0.52 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
November | kL |  |  | mg/L = milligrams per litre
Data | 30 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 2568
Mean | 4252
Median | 4111
Maximum | 7328
Date Data Published: |  |  | 2020-11-18
Summary of results for: |  |  | October
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 27/10/2020 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 06/11/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.1 |  | 6.5 - 8.5 | pH | No
| TSS | 8 | 15 | 30 | mg/L | No
| Faecal Coliforms | 3 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.55 | 2 | 5 | mg/L | No
| Total P | 0.27 | 0.5 | 1 | mg/L | No
| Total N | 2.17 | 10 | 15 | mg/L | No
| Aluminium | 0.45 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
October | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 3136
Mean | 4300
Median | 3403
Maximum | 12,357**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-10-16
Summary of results for: |  |  | 2020-21
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 3
Environment Monitoring 100 metres upstream of the confluence between the discharge channel and Farmers Creek
|  | Pollutant | Measurement | Units
Sampled | 2020-09-29 | BOD | <2 | mg/L
Obtained | 2020-10-08 | Oil & Grease | <5 | mg/L
|  | pH | 7.4
|  | TSS | <2 | mg/L
|  | Faecal Coliforms | 15 | cfu/100mL
|  | Ammonia | 0.01 | mg/L
|  | Total P | 0.008 | mg/L
|  | Total N | 0.8 | mg/L
|  | Aluminium | 0.14 | mg/L
Date Data Published: |  |  | 2020-10-16
Summary of results for: |  |  | 2020-21
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 4
Environment Monitoring 200 metres downstream of the confluence between the discharge channel and Farmers Creek
|  | Pollutant | Measurement | Units
Sampled | 2020-09-29 | BOD | <2 | mg/L
Obtained | 2020-10-08 | Oil & Grease | <5 | mg/L
|  | pH | 7.4
|  | TSS | 4 | mg/L
|  | Faecal Coliforms | ~73 | cfu/100mL
|  | Ammonia | 0.14 | mg/L
|  | Total P | 0.058 | mg/L
|  | Total N | 1.62 | mg/L
|  | Aluminium | 0.18 | mg/L
Date Data Published: |  |  | 2020-10-16
Summary of results for: |  |  | September
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 29/09/2020 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 08/10/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.1 |  | 6.5 - 8.5 | pH | No
| TSS | 10 | 15 | 30 | mg/L | No
| Faecal Coliforms | 2 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.74 | 2 | 5 | mg/L | No
| Total P | 0.499 | 0.5 | 1 | mg/L | No
| Total N | 4.7 | 10 | 15 | mg/L | No
| Aluminium | 0.54 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
September | kL |  |  | mg/L = milligrams per litre
Data | 30 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 3964
Mean | 4840
Median | 4637
Maximum | 7321
Date Data Published: |  |  | 2020-09-09
Summary of results for: |  |  | August
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 25/08/2020 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 04/09/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7 |  | 6.5 - 8.5 | pH | No
| TSS | 3 | 15 | 30 | mg/L | No
| Faecal Coliforms | 3 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.17 | 2 | 5 | mg/L | No
| Total P | 0.17 | 0.5 | 1 | mg/L | No
| Total N | 6.01 | 10 | 15 | mg/L | No
| Aluminium | 0.16 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
August | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 4975
Mean | 10790
Median | 8419
Maximum | 31,072**
**Note. There were five periods in the month of August where rainfall exceeded 15mm in a 24hr period. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-08-12
Summary of results for: |  |  | July
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 29/07/2020 | BOD | 8 | 10 | 15 | mg/L | No
Obtained 11/08/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 6.8 |  | 6.5 - 8.5 | pH | No
| TSS | 67 | 15 | 30 | mg/L | Yes | Wet weather event experienced. Increased flows has caused carryover in the IDEA Tank
| Faecal Coliforms | 20 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.12 | 2 | 5 | mg/L | No
| Total P | 0.72 | 0.5 | 1 | mg/L | No
| Total N | 6.24 | 10 | 15 | mg/L | No
| Aluminium | 1.15 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
July | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 3066
Mean | 5977
Median | 3437
Maximum | 29,128**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-07-16
Summary of results for: |  |  | June
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 23/06/2020 | BOD | 7 | 10 | 15 | mg/L | No
Obtained 16/07/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.4 |  | 6.5 - 8.5 | pH | No
| TSS | 2 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | <0.01 | 2 | 5 | mg/L | No
| Total P | 0.108 | 0.5 | 1 | mg/L | No
| Total N | 1.38 | 10 | 15 | mg/L | No
| Aluminium | 0.13 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
June | kL |  |  | mg/L = milligrams per litre
Data | 30 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 3293
Mean | 4172
Median | 3954
Maximum | 7097
Date Data Published: |  |  | 2020-06-11
Summary of results for: |  |  | May
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 27/05/2020 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 04/06/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.2 |  | 6.5 - 8.5 | pH | No
| TSS | 3 | 15 | 30 | mg/L | No
| Faecal Coliforms | 2 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.41 | 2 | 5 | mg/L | No
| Total P | 0.298 | 0.5 | 1 | mg/L | No
| Total N | 3.29 | 10 | 15 | mg/L | No
| Aluminium | 0.17 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
May | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 3762
Mean | 4874
Median | 4656
Maximum | 9508
Date Data Published: |  |  | 2020-05-19
Summary of results for: |  |  | April
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 28/04/2020 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 06/05/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.2 |  | 6.5 - 8.5 | pH | No
| TSS | 2 | 15 | 30 | mg/L | No
| Faecal Coliforms | 1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.23 | 2 | 5 | mg/L | No
| Total P | 0.104 | 0.5 | 1 | mg/L | No
| Total N | 6.25 | 10 | 15 | mg/L | No
| Aluminium | 0.19 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
April | kL |  |  | mg/L = milligrams per litre
Data | 30 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 3247
Mean | 5511
Median | 4617
Maximum | 21,675**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-04-17
Summary of results for: |  |  | March
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 25/03/2020 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 03/04/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.2 |  | 6.5 - 8.5 | pH | No
| TSS | <2 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.14 | 2 | 5 | mg/L | No
| Total P | 0.095 | 0.5 | 1 | mg/L | No
| Total N | 5.92 | 10 | 15 | mg/L | No
| Aluminium | 0.05 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
March | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 3262
Mean | 5329
Median | 4781
Maximum | 13732
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-03-19
Summary of results for: |  |  | February
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 26/02/2020 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 06/03/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.2 |  | 6.5 - 8.5 | pH | No
| TSS | 3 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.04 | 2 | 5 | mg/L | No
| Total P | 0.132 | 0.5 | 1 | mg/L | No
| Total N | 6.9 | 10 | 15 | mg/L | No
| Aluminium | 0.14 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
February | kL |  |  | mg/L = milligrams per litre
Data | 29 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 1932
Mean | 7931
Median | 5032
Maximum | 35,253**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-02-25
Summary of results for: |  |  | January
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 29/01/2020 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 12/02/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.1 |  | 6.5 - 8.5 | pH | No
| TSS | 2 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 1.67 | 2 | 5 | mg/L | No
| Total P | 0.11 | 0.5 | 1 | mg/L | No
| Total N | 4.08 | 10 | 15 | mg/L | No
| Aluminium | 0.22 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
January | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 1568
Mean | 2347
Median | 1977
Maximum | 7680

## 2019
Lithgow Sewage Treatment Plant
Date Data Published: |  |  | 2020-01-08
Summary of results for: |  |  | December
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 18/12/2019 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 06/01/2020 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.2 |  | 6.5 - 8.5 | pH | No
| TSS | 4 | 15 | 30 | mg/L | No
| Faecal Coliforms | 2 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.31 | 2 | 5 | mg/L | No
| Total P | 0.16 | 0.5 | 1 | mg/L | No
| Total N | 2.4 | 10 | 15 | mg/L | No
| Aluminium | 0.21 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
December | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 1248
Mean | 2262
Median | 2259
Maximum | 2930
Date Data Published: |  |  | 2019-12-09
Summary of results for: |  |  | November
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 27/11/2019 | BOD | 3 | 10 | 15 | mg/L | No
Obtained 4/12/2019 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.1 |  | 6.5 - 8.5 | pH | No
| TSS | 6 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.01 | 2 | 5 | mg/L | No
| Total P | 0.223 | 0.5 | 1 | mg/L | No
| Total N | 1.77 | 10 | 15 | mg/L | No
| Aluminium | 0.3 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
November | kL |  |  | mg/L = milligrams per litre
Data | 30 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 2201
Mean | 2776
Median | 2726
Maximum | 4076
Date Data Published: |  |  | 2019-11-13
Summary of results for: |  |  | 2019-20
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 3
Environment Monitoring 100 metres upstream of Point 1
|  | Pollutant | Measurement | Units
Sampled | 2019-10-29 | BOD | 4 | mg/L
Obtained | 2019-11-12 | Oil & Grease | <5 | mg/L
Published | 2019-11-13 | pH | 7.4
|  | TSS | 6 | mg/L
|  | Faecal Coliforms | ~9500 | cfu/100mL
|  | Ammonia | <0.01 | mg/L
|  | Total P | 0.049 | mg/L
|  | Total N | 0.83 | mg/L
|  | Aluminium | 0.16 | mg/L
Date Data Published: |  |  | 2019-11-13
Summary of results for: |  |  | 2019-20
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 4
Environment Monitoring 200 metres downstream of Point 1
|  | Pollutant | Measurement | Units
Sampled | 2019-10-29 | BOD | 3 | mg/L
Obtained | 2019-11-12 | Oil & Grease | <5 | mg/L
Published | 2019-11-13 | pH | 7.3
|  | TSS | 50 | mg/L
|  | Faecal Coliforms | ~5200 | cfu/100mL
|  | Ammonia | 0.28 | mg/L
|  | Total P | 0.75 | mg/L
|  | Total N | 3.33 | mg/L
|  | Aluminium | 2.22 | mg/L
Date Data Published: |  |  | 2019-11-13
Summary of results for: |  |  | October
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 29/10/2019 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 12/11/2019 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7 |  | 6.5 - 8.5 | pH | No
| TSS | 11 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.06 | 2 | 5 | mg/L | No
| Total P | 0.505 | 0.5 | 1 | mg/L | No
| Total N | 4.02 | 10 | 15 | mg/L | No
| Aluminium | 0.5 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
October | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 1238
Mean | 3308
Median | 3485
Maximum | 4631
Date Data Published: |  |  | 2019-10-21
Summary of results for: |  |  | September
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
| BOD |  | 10 | 15 | mg/L | No | Plant was not discharging to the environment at the time of routine sample. Discharge to the environment occured 1 September to 10 September and on 24 September. On the remaining dates in September, the plant was discharging to storage lagoons. Discharging to the storage lagoons was undertaken while adjustments were being made to ensure licence limits would not be breached. This is in accordance with Condition O - 4.2 of the Licence.
| Oil & Grease |  | 5 | 10 | mg/L | No
| pH |  |  | 6.5 - 8.5 | pH | No
| TSS |  | 15 | 30 | mg/L | No
| Faecal Coliforms |  | 200 | 600 | cfu/100mL | No
| Ammonia |  | 2 | 5 | mg/L | No
| Total P |  | 0.5 | 1 | mg/L | No
| Total N |  | 10 | 15 | mg/L | No
| Aluminium |  |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
September | kL |  |  | mg/L = milligrams per litre
Data | 11** |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 3003
Mean | 3438
Median | 3284
Maximum | 4734
**Note. Discharge to the environment was undertaken for a total of 11 days in September 2019 (01/09/19 - 10/09/19 & 24/09/19).
Date Data Published: |  |  | 2019-09-11
Summary of results for: |  |  | August
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 28/08/2019 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 06/09/2019 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.5 |  | 6.5 - 8.5 | pH | No
| TSS | 4 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.66 | 2 | 5 | mg/L | No
| Total P | 0.228 | 0.5 | 1 | mg/L | No
| Total N | 2.98 | 10 | 15 | mg/L | No
| Aluminium | 0.11 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
August | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 2935
Mean | 3479
Median | 3337
Maximum | 5156
Date Data Published: |  |  | 2019-08-13
Summary of results for: |  |  | July
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  |  |  | EPL no. 236
| Pollutant | Measurement | 90 Percentile Limit | 100 Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 31/07/2019 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 07/08/2019 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7 |  | 6.5 - 8.5 | pH | No
| TSS | 7 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 1.21 | 2 | 5 | mg/L | No
| Total P | 0.372 | 0.5 | 1 | mg/L | No
| Total N | 4.08 | 10 | 15 | mg/L | No
| Aluminium | 0.22 |  |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
July | kL |  |  | mg/L = milligrams per litre
Data | 14** |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 3250
Mean | 3605
Median | 3462
Maximum | 5033
**Note. Discharge to the environment was undertaken for a total of 14 days in July 2019 (18/07/19 - 31/07/19).
Date Data Published: |  |  | 2019-07-23
Summary of results for: |  |  | 2018-19
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 7
Tertiary Lagoon Number 3
|  | Pollutant | Measurement | Units
Sampled | 2018-06-26 | BOD | 7 | mg/L
Obtained | 2018-07-16 | Oil & Grease | <5 | mg/L
Published | 2019-07-17 | pH | 9.1
|  | TSS | 16 | mg/L
|  | Faecal Coliforms | 28 | cfu/100mL
|  | Ammonia | 0.05 | mg/L
|  | Total P | 0.545 | mg/L
|  | Total N | 2.54 | mg/L
|  | Aluminium | 0.15 | mg/L
Date Data Published: |  |  | 2019-07-23
Summary of results for: |  |  | June
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  | EPL no. 236
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 26/06/2019 | BOD | <2 | 10 | mg/L | No
Obtained 16/07/2019 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7.5 | 6.5 - 8.5 |  | No
| TSS | 3 | 15 | mg/L | No
| Faecal Coliforms | 1 | 200 | cfu/100mL | No
| Ammonia | 0.51 | 5 | mg/L | No
| Total P | 0.181 | 0.5 | mg/L | No
| Total N | 7.09 | 15 | mg/L | No
| Aluminium | 0.05 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
June | kL |  |  | mg/L = milligrams per litre
Data | 30 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 2096
Mean | 3221
Median | 2921
Maximum | 4807
Date Data Published: |  |  | 2019-06-17
Summary of results for: |  |  | May
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  | EPL no. 236
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 29/05/2019 | BOD | <2 | 10 | mg/L | No
Obtained 8/06/2019 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7.2 | 6.5 - 8.5 |  | No
| TSS | <2 | 15 | mg/L | No
| Faecal Coliforms | 1 | 200 | cfu/100mL | No
| Ammonia | 0.79 | 5 | mg/L | No
| Total P | 0.103 | 0.5 | mg/L | No
| Total N | 8.14 | 15 | mg/L | No
| Aluminium | 0.08 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
May | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 2157
Mean | 2957
Median | 2627
Maximum | 6354
Correction Log - Aluminium results not previously recorded, previous reports amended with results.
Date Data Published: |  |  | 2019-05-16
Summary of results for: |  |  | April
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  | EPL no. 236
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 23/04/2019 | BOD | <2 | 10 | mg/L | No
Obtained 6/05/2019 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7.2 | 6.5 - 8.5 |  | No
| TSS | 2 | 15 | mg/L | No
| Faecal Coliforms | 8 | 200 | cfu/100mL | No
| Ammonia | 0.38 | 5 | mg/L | No
| Total P | 0.076 | 0.5 | mg/L | No
| Total N | 4.77 | 15 | mg/L | No
| Aluminium | 0.1 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
April | kL |  |  | mg/L = milligrams per litre
Data | 30 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 2887
Mean | 3485
Median | 3431
Maximum | 4579
Date Data Published: |  |  | 2019-04-15
Summary of results for: |  |  | March
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  | EPL no. 236
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 26/03/2019 | BOD | <2 | 10 | mg/L | No
Obtained 8/04/2019 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7.3 | 6.5 - 8.5 |  | No
| TSS | <2 | 15 | mg/L | No
| Faecal Coliforms | <1 | 200 | cfu/100mL | No
| Ammonia | 0.2 | 5 | mg/L | No
| Total P | 0.065 | 0.5 | mg/L | No
| Total N | 3.81 | 15 | mg/L | No
| Aluminium | 0.08 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
March | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 1611
Mean | 3831
Median | 3004
Maximum | 11309
Date Data Published: |  |  | 2019-03-14
Summary of results for: |  |  | February
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  | EPL no. 236
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 26/02/19 | BOD | <2 | 10 | mg/L | No
Obtained 08/03/19 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7.1 | 6.5 - 8.5 |  | No
| TSS | <2 | 15 | mg/L | No
| Faecal Coliforms | <1 | 200 | cfu/100mL | No
| Ammonia | 0.3 | 5 | mg/L | No
| Total P | 0.089 | 0.5 | mg/L | No
| Total N | 6.44 | 15 | mg/L | No
| Aluminium | 0.1 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
February | kL |  |  | mg/L = milligrams per litre
Data | 28 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 2346
Mean | 3088
Median | 3077
Maximum | 3921
Date Data Published: |  |  | 2019-02-07
Summary of results for: |  |  | January
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  | EPL no. 236
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 29/01/19 | BOD | <2 | 10 | mg/L | No
Obtained 6/02/19 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7.4 | 6.5 - 8.5 |  | No
| TSS | 3 | 15 | mg/L | No
| Faecal Coliforms | 1 | 200 | cfu/100mL | No
| Ammonia | 0.38 | 5 | mg/L | No
| Total P | 0.085 | 0.5 | mg/L | No
| Total N | 1.8 | 15 | mg/L | No
| Aluminium | 0.25 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
January | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 3182
Mean | 4909
Median | 4342
Maximum | 14863

## 2018
Lithgow Sewage Treatment Plant
Date Data Published: |  |  | 2019-01-10
Summary of results for: |  |  | December
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  | EPL no. 236
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 18/12/18 | BOD | <2 | 10 | mg/L | No
Obtained 5/01/19 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7.5 | 6.5 - 8.5 |  | No
| TSS | 4 | 15 | mg/L | No
| Faecal Coliforms | 3 | 200 | cfu/100mL | No
| Ammonia | 0.13 | 5 | mg/L | No
| Total P | 0.011 | 0.5 | mg/L | No
| Total N | 1.22 | 15 | mg/L | No
| Aluminium | 0.5 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
December | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 2852
Mean | 6017
Median | 4641
Maximum | 23551
Date Data Published: |  |  | 2018-12-07
Summary of results for: |  |  | November
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  | EPL no. 236
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 27/11/18 | BOD | <2 | 10 | mg/L | No
Obtained 6/12/18 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7.2 | 6.5 - 8.5 |  | No
| TSS | 16 | 15 | mg/L | No
| Faecal Coliforms | <1 | 200 | cfu/100mL | No
| Ammonia | 1.07 | 5 | mg/L | No
| Total P | 0.46 | 0.5 | mg/L | No
| Total N | 3.22 | 15 | mg/L | No
| Aluminium | 1.39 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
November | kL |  |  | mg/L = milligrams per litre
Data | 30 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 2579
Mean | 4141
Median | 2866
Maximum | 23191
Date Data Published: |  |  | 2018-11-12
Summary of results for: |  |  | October
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Farmers Creek
Licensee: Lithgow City Council |  |  | EPL no. 236
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 30/10/18 | BOD | 2 | 10 | mg/L | No
Obtained 10/11/18 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7.2 | 6.5 - 8.5 |  | No
| TSS | 6 | 15 | mg/L | No
| Faecal Coliforms | 5 | 200 | cfu/100mL | No
| Ammonia | 0.65 | 5 | mg/L | No
| Total P | 0.171 | 0.5 | mg/L | No
| Total N | 3.18 | 15 | mg/L | No
| Aluminium | 0.65 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
October | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 2320
Mean | 4609
Median | 3806
Maximum | 10580
Date Data Published: |  |  | 2018-11-12
Summary of results for: |  |  | 2018-19
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 3
Environment Monitoring 100 metres upstream of Point 1
|  | Pollutant | Measurement | Units
Sampled | 2018-08-28 | BOD | <2 | mg/L
Obtained | 2018-09-05 | Oil & Grease | <5 | mg/L
|  | pH | 7.5
|  | TSS | <2 | mg/L
|  | Faecal Coliforms | 130 | cfu/100mL
|  | Ammonia | 0.03 | mg/L
|  | Total P | 0.012 | mg/L
|  | Total N | 0.37 | mg/L
|  | Aluminium | 0.15 | mg/L
Date Data Published: |  |  | 2018-11-12
Summary of results for: |  |  | 2018-19
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 4
Environment Monitoring 200 metres downstream of Point 1
|  | Pollutant | Measurement | Units
Sampled | 2018-08-28 | BOD | <2 | mg/L
Obtained | 2018-09-05 | Oil & Grease | <5 | mg/L
Published |  | pH | 7.2
|  | TSS | <2 | mg/L
|  | Faecal Coliforms | 53 | cfu/100mL
|  | Ammonia | 0.2 | mg/L
|  | Total P | 0.041 | mg/L
|  | Total N | 6.64 | mg/L
|  | Aluminium | 0.12 | mg/L
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-09-25 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-10-03 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-10-08 | pH | 7.2 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | <2 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.28 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.108 | 0.5 | mg/L |  |  |  |  | No
|  | Total N | 9.41 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.2 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 30 | 2274 | 6702 | 3137 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-08-28 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-09-06 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-09-07 | pH | 7 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 2 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.24 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.094 | 0.5 | mg/L |  |  |  |  | No
|  | Total N | 13.1 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.17 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 1812 | 3780 | 2466 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-07-24 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-08-01 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-08-15 | pH | 7.2 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.78 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.149 | 0.5 | mg/L |  |  |  |  | No
|  | Total N | 5.96 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.33 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 2111 | 3947 | 2485 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-06-26 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-07-04 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-07-09 | pH | 7.1 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 4 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.66 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.105 | 0.5 | mg/L |  |  |  |  | No
|  | Total N | 9.43 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.28 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 29 | 2236 | 4474 | 2793 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-05-29 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-06-07 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-06-13 | pH | 7.3 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 2 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.02 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.1 | 0.5 | mg/L |  |  |  |  | No
|  | Total N | 8.49 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.22 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 1851 | 3575 | 2961 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-04-17 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-04-27 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-05-16 | pH | 7.2 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 13 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 1.79 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.252 | 0.5 | mg/L |  |  |  |  | No
|  | Total N | 8.57 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.33 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 29 | 2872 | 3669 | 3187 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-03-28 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-04-07 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-04-13 | pH | 7.2 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 9 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 2 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.19 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.2 | 0.5 | mg/L |  |  |  |  | No
|  | Total N | 5.91 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.62 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 25 | 2840 | 5373 | 3722 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-02-27 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-03-10 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-03-16 | pH | 7.2 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 9 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 2 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.28 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.354 | 0.5 | mg/L |  |  |  |  | No
|  | Total N | 6.25 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.64 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 28 | 2424 | 11299 | 3769 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-01-30 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-03-08 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-03-16 | pH | 7.4 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 4 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 6 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.65 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.116 | 0.5 | mg/L |  |  |  |  | No
|  | Total N | 2.4 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.33 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 2510 | 6982 | 3458 | No
0

## 2017
Lithgow Sewage Treatment Plant
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-12-20 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-12-30 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-01-11 | pH | 7.3 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 13 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.64 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.176 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 2.66 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.44 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 2013 | 6739 | 3279 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-11-28 | BOD | 2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-12-12 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-12-15 | pH | 7.4 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 4 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.76 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.167 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 3.42 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.37 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 30 | 1988 | 3772 | 2761 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-10-24 | BOD | 2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-11-04 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-11-07 | pH | 7.3 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 8 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 27 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.8 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.425 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 4.6 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.58 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 1561 | 14233 | 3243 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-09-27 | BOD | 2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-10-06 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-10-10 | pH | 7.3 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 1800 | 200 | cfu/100mL |  |  |  |  | Yes
|  | Ammonia | 1.2 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.19 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 4.89 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.44 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 30 | 2312 | 3351 | 2965 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-08-29 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-09-11 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-09-12 | pH | 7.2 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 3 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 1.41 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.158 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 6.64 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.32 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 3038 | 4892 | 3560 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-07-26 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-08-04 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-08-14 | pH | 7 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 9 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 2.62 | 5 | mg/L |  |  |  |  | No
|  | Total P | 0.135 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 11.4 | 15 | mg/L |  |  |  |  | No
|  | Aluminium | 0.28 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 2896 | 4287 | 3408 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-06-27 | BOD | 8 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-07-05 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-07-10 | pH | 7.08 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | <5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 38 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.53 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.24 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 2.63 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.49 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 30 | 2859 | 6642 | 4511 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-05-24 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-05-30 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-06-09 | pH | 6.93 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | <5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 2 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.34 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.07 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 4.28 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.12 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 2255 | 6875 | 3561 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-04-19 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-04-26 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-05-11 | pH | 6.79 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | <5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 120 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.11 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.07 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 4.7 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.14 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 30 | 1986 | 8362 | 4518 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-03-22 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-03-30 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-04-07 | pH | 6.3 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | <5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 2 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.16 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.17 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 7.4 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.37 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 2978 | 18421 | 5825 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-02-21 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-03-07 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-03-14 | pH | 7.38 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | <5 | 15 | mg/L |  |  |  |  | No
Samples taken with no
|  | Faecal Coliforms |  | 200 | cfu/100mL |  |  |  |  | discharge to environment.
|  | Ammonia | 0.31 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.1 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 4.3 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.29 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 28 | 2069 | 4859 | 2750 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-01-18 | BOD | 4 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-01-31 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-02-13 | pH | 7.1 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | <5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms |  | 200 | cfu/100mL |  |  |  |  | Samples taken with no
discharge to environment.
|  | Ammonia | 4.67 | 2 | mg/L |  |  |  |  | Yes
|  | Total P | 0.33 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 1.94 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.42 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 2305 | 4416 | 2998 | No

## 2016
Lithgow Sewage Treatment Plant
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-12-20 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-01-03 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-01-16 | pH | 7.2 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 18 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 52 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 1.23 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.81 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 7.4 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 1.11 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 2783 | 4603 | 3445 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-11-15 | BOD | 2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-11-23 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-12-15 | pH | 6.5 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | <5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.5 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.36 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 9.5 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.23 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 30 | 2783 | 4603 | 3445 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-10-18 | BOD | 6 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-11-01 | Oil & Grease | 7 | 10 | mg/L |  |  |  |  | No
Published | 2016-11-11 | pH | 7.2 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 1300 | 200 | cfu/100mL |  |  |  |  | Yes
|  | Ammonia | 4.53 | 2 | mg/L |  |  |  |  | Yes
|  | Total P | 0.19 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 8.3 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.42 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 3200 | 8568 | 4285 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-09-20 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-10-20 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-11-01 | pH | 7.16 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | <5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.49 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.15 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 2.6 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.19 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 30 | 5994 | 16130 | 8379 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-08-23 | BOD | 5 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-08-31 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-09-12 | pH | 7.06 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | <5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.11 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.14 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 8.7 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.1 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 726 | 13974 | 6030 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-07-26 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-08-03 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-08-12 | pH | 6.9 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | <5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <2 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.14 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.1 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 7.6 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.17 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 4120 | 14054 | 6470 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-06-28 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-07-09 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-07-21 | pH | 6.8 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.2 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.121 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 8.27 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.15 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 30 | 2093 | 14933 | 5958 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-06-07 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-06-29 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-07-21 | pH | 6.8 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 2 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | 3 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.2 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.13 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 7.36 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.27 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 2095 | 3397 | 2369 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-04-26 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-05-06 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-05-10 | pH | 7.3 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 4 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | <0.1 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.338 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 3.61 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.27 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 30 | 2231 | 2608 | 2384 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-03-29 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-04-13 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-04-20 | pH | 7.1 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | <0.1 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.2 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 2.74 | 10 | mg/L |  |  |  |  | Yes
|  | Aluminium | 0.6 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 |  |  |  | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-02-23 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-03-16 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-03-22 | pH | 6.8 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 5 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.6 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.18 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 12.6 | 10 | mg/L |  |  |  |  | Yes
|  | Aluminium | 0.34 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 29 | 1505 | 8880 | 4089 | No
Sampling point: A |  |  | EPL no. 236 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measure-ment | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-01-19 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-02-01 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-02-05 | pH | 7.3 | 6.5 - 8.5 | [5 empty] | No
|  | TSS | 4 | 15 | mg/L |  |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL |  |  |  |  | No
|  | Ammonia | 0.1 | 2 | mg/L |  |  |  |  | No
|  | Total P | 0.215 | 0.5 | mg/L 90 percentile |  |  |  |  | No
|  | Total N | 8.01 | 10 | mg/L |  |  |  |  | No
|  | Aluminium | 0.24 |  | mg/L
|  | Daily Flow |  | 30000 | kL/day | 31 | 2483 | 12089 | 5624 | No