## 2026
Wallerawang Sewerage Treatment Plant
| Date Data Published: |  |  | 2026-07-03
| Summary of results for: |  |  | 2026-06-01
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2026-06-23 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2026-07-02 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | <2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.14 | n/a | n/a | mg/L | No
|  | Faecal coliforms | 10 | 200 | 600 | CFU/100ml | No
|  | Total N | 6.86 | 10 | 15 | mg/L | No
|  | Total P | 0.135 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.31 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| 2026-06-01 | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 362
| Maximum | 923
| Mean | 536.46
| Median | 504.5
Wallerawang Sewerage Treatment Plant
| Date Data Published: |  |  | 2026-04-21
| Summary of results for: |  |  | 2026-04-01
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2026-03-24 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2026-03-25 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | <2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.17 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.81 | 10 | 15 | mg/L | No
|  | Total P | 0.1 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.4 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| 2026-02-01 | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 336
| Maximum | 569
| Mean | 445.3667
| Median | 439
Wallerawang Sewerage Treatment Plant
| Date Data Published: |  |  | 2026-03-12
| Summary of results for: |  |  | 2026-03-01
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2026-03-24 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2026-03-25 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Aluminium | 0.19 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 5.69 | 10 | 15 | mg/L | No
|  | Total P | 0.131 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.16 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| 2026-02-01 | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 348
| Maximum | 1510**
| Mean | 585
| Median | 535
*heavy rainfall event leading to maximum discharge
Wallerawang Sewerage Treatment Plant
| Date Data Published: |  |  | 2026-03-12
| Summary of results for: |  |  | 2026-02-01
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2026-02-24 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2026-02-25 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Aluminium | 0.19 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 5.69 | 10 | 15 | mg/L | No
|  | Total P | 0.131 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.16 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| 2026-02-01 | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 285
| Maximum | 770
| Mean | 431
| Median | 397
| Date Data Published: |  |  | 2026-03-12
| Summary of results for: |  |  | 2026-01-01
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2026-01-27 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2026-01-28 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Aluminium | 0.14 | n/a | n/a | mg/L | No
|  | Faecal coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 6.91 | 10 | 15 | mg/L | No
|  | Total P | 0.118 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.54 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| 2026-01-01 | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 273
| Maximum | 709
| Mean | 403
| Median | 384

## 2025
| Date Data Published: |  |  | 2025-03-12
| Summary of results for: |  |  | november
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 25/11/25 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 26/11/25 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 8 |  | 6.5 - 8.5 |  | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.24 | n/a | n/a | mg/L | No
|  | Faecal coliforms | 3 | 200 | 600 | CFU/100ml | No
|  | Total N | 5.07 | 10 | 15 | mg/L | No
|  | Total P | 0.117 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.05 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| November | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 246
| Maximum | 688
| Mean | 471
| Median | 472
| Date Data Published: |  |  | 2025-08-10
| Summary of results for: |  |  | September
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 30/9/25 | BOD | 2 | 10 | 15 | mg/L | No
Result Obtained | 2025-01-10 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Aluminium | 0.23 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.81 | 10 | 15 | mg/L | No
|  | Total P | 0.279 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.31 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| November | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 404
| Maximum | 1793
| Mean | 765 | [5 empty] | *heavy rainfall event leading to maximum discharge
| Median | 699
| Date Data Published: |  |  | 2025-03-09
| Summary of results for: |  |  | August
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 26/8/25 | BOD | 5 | 10 | 15 | mg/L | No
Result Obtained | 27/8/25 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.1 | n/a | n/a | mg/L | No
|  | Faecal coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.3 | 10 | 15 | mg/L | No
|  | Total P | 0.124 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.2 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| November | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 489
| Maximum | 1797
| Mean | 871 | [5 empty] | *heavy rainfall event leading to maximum discharge
| Median | 759
| Date Data Published: |  |  | 2025-06-08
| Summary of results for: |  |  | July
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 29/7/25 | BOD | 5 | 10 | 15 | mg/L | No
Result Obtained | 30/7/25 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | <2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.14 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.65 | 10 | 15 | mg/L | No
|  | Total P | 0.111 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.16 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| November | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 374
| Maximum | 1448
| Mean | 631 | [5 empty] | *heavy rainfall event leading to maximum discharge
| Median | 561
| Date Data Published: |  |  | 2025-01-07
| Summary of results for: |  |  | June
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 24/6/25 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 25/6/25 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.2 |  | 6.5 - 8.5 |  | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.15 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.62 | 10 | 15 | mg/L | No
|  | Total P | 0.12 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.01 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| November | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 305
| Maximum | 601
| Mean | 445
| Median | 423
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Result Obtained | 2025-04-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.2 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Aluminium | 0.23 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.44 | 10 | 15 | mg/L | No
|  | Total P | 0.126 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.22 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| November | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 322
| Maximum | 747
| Mean | 462
| Median | 417
| Date Data Published: |  |  | 2025-07-05
| Summary of results for: |  |  | April
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 29/4/2025 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2025-07-05 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.2 |  | 6.5 - 8.5 |  | No
|  | TSS | <2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.3 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.97 | 10 | 15 | mg/L | No
|  | Total P | 0.131 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.07 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| November | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 317
| Maximum | 1039**
| Mean | 422
| Median | 398
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2025-04-02
| Summary of results for: |  |  | March
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2025-03-25 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2025-03-26 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.21 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.83 | 10 | 15 | mg/L | No
|  | Total P | 0.097 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.06 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| November | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 272
| Maximum | 644
| Mean | 401
| Median | 391
| Date Data Published: |  |  | 2025-03-07
| Summary of results for: |  |  | February
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2025-02-26 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2025-03-05 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Aluminium | 0.31 | n/a | n/a | mg/L | No
|  | Faecal coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.98 | 10 | 15 | mg/L | No
|  | Total P | 0.151 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.09 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| November | kL |  |  |  | mg/L = milligrams per litre
| Data | 28 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 273
| Maximum | 1041**
| Mean | 477
| Median | 425
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.

## 2024
| Date Data Published: |  |  | 2025-02-10
| Summary of results for: |  |  | January
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2025-01-29 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2025-02-05 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Aluminium | 0.2 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.61 | 10 | 15 | mg/L | No
|  | Total P | 0.139 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.21 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| November | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 118
| Maximum | 1061**
| Mean | 507
| Median | 481
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2024-12-06
| Summary of results for: |  |  | November
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2024-11-26 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2024-12-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Aluminium | 0.24 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.67 | 10 | 15 | mg/L | No
|  | Total P | 0.135 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.04 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| November | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 261
| Maximum | 1700**
| Mean | 460
| Median | 389
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2024-11-08
| Summary of results for: |  |  | October
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2024-10-29 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2024-11-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.3 |  | 6.5 - 8.5 |  | No
|  | TSS | <2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.16 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.54 | 10 | 15 | mg/L | No
|  | Total P | 0.123 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.07 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| October | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 304
| Maximum | 531
| Mean | 412
| Median | 407
| Date Data Published: |  |  | 2024-10-08
| Summary of results for: |  |  | September
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2024-09-24 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2024-10-03 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.17 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.55 | 10 | 15 | mg/L | No
|  | Total P | 0.116 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.09 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| September | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 356
| Maximum | 731
| Mean | 458
| Median | 430
| Date Data Published: |  |  | 2024-09-12
| Summary of results for: |  |  | August
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2024-08-27 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2024-09-10 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.17 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.55 | 10 | 15 | mg/L | No
|  | Total P | 0.116 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.09 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 405
| Maximum | 873
| Mean | 571
| Median | 555
| Date Data Published: |  |  | 2024-08-19
| Summary of results for: |  |  | July
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2024-07-30 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2024-08-19 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Aluminium | 0.16 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.46 | 10 | 15 | mg/L | No
|  | Total P | 0.099 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.01 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 387
| Maximum | 973
| Mean | 603
| Median | 576
| Date Data Published: |  |  | 2024-07-09
| Summary of results for: |  |  | June
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2024-06-25 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2024-07-04 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.2 |  | 6.5 - 8.5 |  | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Aluminium | 0.27 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.43 | 10 | 15 | mg/L | No
|  | Total P | 0.116 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.51 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 391
| Maximum | 1191**
| Mean | 606
| Median | 590
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2024-07-09
| Summary of results for: |  |  | May
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2024-05-28 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2024-06-08 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.2 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.87 | 10 | 15 | mg/L | No
|  | Total P | 0.104 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.22 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 303
| Maximum | 789
| Mean | 517
| Median | 536
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2024-04-28
| Summary of results for: |  |  | April
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2024-04-23 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2024-05-03 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.16 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.58 | 10 | 15 | mg/L | No
|  | Total P | 0.079 | 0.5 | 1 | mg/L | No
|  | Ammonia | <0.01 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 382
| Maximum | 2024**
| Mean | 670
| Median | 551
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2024-04-18
| Summary of results for: |  |  | March
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2024-03-26 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2024-04-05 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Aluminium | 0.14 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.98 | 10 | 15 | mg/L | No
|  | Total P | 0.148 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.13 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 325
| Maximum | 826
| Mean | 506
| Median | 506
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2024-02-27
| Summary of results for: |  |  | February
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2024-02-27 | BOD | 11 | 10 | 15 | mg/L | Yes
Result Obtained | 2024-03-11 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | <2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.15 | n/a | n/a | mg/L | No
|  | Faecal coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.66 | 10 | 15 | mg/L | No
|  | Total P | 0.074 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.08 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 29 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 421
| Maximum | 1129**
| Mean | 648
| Median | 633
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2024-01-30
| Summary of results for: |  |  | January
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2024-01-30 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2024-02-07 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.2 |  | 6.5 - 8.5 |  | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.17 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.4 | 10 | 15 | mg/L | No
|  | Total P | 0.076 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.1 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 382
| Maximum | 1446**
| Mean | 697
| Median | 657
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.

## 2023
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2023-12-19
| Summary of results for: |  |  | December
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2023-12-19 | BOD | 5 | 10 | 15 | mg/L | No
Result Obtained | 2023-12-28 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.2 |  | 6.5 - 8.5 |  | No
|  | TSS | 6 | 15 | 30 | mg/L | No
|  | Aluminium | 0.38 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.43 | 10 | 15 | mg/L | No
|  | Total P | 0.281 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.26 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 38
| Maximum | 1113
| Mean | 484
| Median | 429
| Date Data Published: |  |  | 2023-11-12
| Summary of results for: |  |  | November
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2023-11-28 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2023-12-07 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.4 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Aluminium | 0.29 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.73 | 10 | 15 | mg/L | No
|  | Total P | 0.194 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.04 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 300
| Maximum | 1038**
| Mean | 439
| Median | 382
| Date Data Published: |  |  | 2023-10-26
| Summary of results for: |  |  | September
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2023-09-26 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2023-10-04 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.3 |  | 6.5 - 8.5 |  | No
|  | TSS | 36 | 15 | 30 | mg/L | No
|  | Aluminium | 0.26 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.56 | 10 | 15 | mg/L | No
|  | Total P | 0.122 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.26 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 186
| Maximum | 633
| Mean | 463
| Median | 453
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2023-09-07
| Summary of results for: |  |  | August
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2023-08-29 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2023-08-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.3 |  | 6.5 - 8.5 |  | No
|  | TSS | 17 | 15 | 30 | mg/L | No | Non-compliance August 2023 due to carry over from a split in one of the Rubber Membranes at the Decant Bridge which caused carry over of sludge, flow was diverted to the holding Ponds on the 24th August. Flow was diverted back to creek on the 3rd of September when test results were back under EPA licence limits, Leichardt Engineering was on site 1st September to replace Rubber Membranes on Decant Bridge
|  | Aluminium | 0.97 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.02 | 10 | 15 | mg/L | No
|  | Total P | 0.52 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.08 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 172
| Maximum | 802
| Mean | 421.9
| Median | 392
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2023-07-08
| Summary of results for: |  |  | July
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2023-07-26 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2023-08-03 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.3 |  | 6.5 - 8.5 |  | No
|  | TSS | 9 | 15 | 30 | mg/L | No
|  | Aluminium | 1.12 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.91 | 10 | 15 | mg/L | No
|  | Total P | 0.56 | 0.5 | 1 | mg/L | No
|  | Ammonia | 1.02 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 29 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 307
| Maximum | 538
| Mean | 420
| Median | 414
Sample Point 3
|  | Pollutant | Measurement | Units
| 2023-07-26 | BOD | <2 | mg/L
| 2023-08-03 | Oil & Grease | <5 | mg/L
|  | pH | 8 | pH
|  | TSS | 4 | mg/L
|  | Total Aluminium | 0.13 | mg/L
|  | Faecal Coliforms | 15 | cfu/100mL
|  | Total N | 0.23 | mg/L
|  | Total P | 0.007 | mg/L
|  | Ammonia | 0.01 | mg/L
Sample Point 4
|  | Pollutant | Measurement | Units
| 2023-07-26 | BOD | <2 | mg/L
| 2023-08-03 | Oil & Grease | <5 | mg/L
|  | pH | 7.6 | pH
|  | TSS | 63 | mg/L
|  | Total Aluminium | 1.44 | mg/L
|  | Faecal Coliforms | ~70 | cfu/100mL
|  | Total N | 1.11 | mg/L
|  | Total P | 0.187 | mg/L
|  | Ammonia | 0.22 | mg/L
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2023-07-07
| Summary of results for: |  |  | June
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2023-06-27 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2023-07-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.2 |  | 6.5 - 8.5 |  | No
|  | TSS | 6 | 15 | 30 | mg/L | No
|  | Aluminium | 0.27 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.96 | 10 | 15 | mg/L | No
|  | Total P | 0.25 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.51 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 29 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 294
| Maximum | 759
| Mean | 401
| Median | 391
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2023-06-16
| Summary of results for: |  |  | May
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2023-05-30 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2023-06-08 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.2 |  | 6.5 - 8.5 |  | No
|  | TSS | 6 | 15 | 30 | mg/L | No
|  | Aluminium | 0.37 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.13 | 10 | 15 | mg/L | No
|  | Total P | 0.177 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.02 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| May | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 294
| Maximum | 567
| Mean | 425
| Median | 415
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2023-05-05
| Summary of results for: |  |  | April
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2023-04-18 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2023-04-27 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.3 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Aluminium | 0.23 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.45 | 10 | 15 | mg/L | No
|  | Total P | 0.16 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.43 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| April | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 358
| Maximum | 856
| Mean | 466
| Median | 416
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2023-04-11
| Summary of results for: |  |  | March
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2023-03-28 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2023-04-05 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.4 |  | 6.5 - 8.5 |  | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Aluminium | 0.17 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.09 | 10 | 15 | mg/L | No
|  | Total P | 0.134 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.12 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 270
| Maximum | 891
| Mean | 468
| Median | 427
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2023-03-10
| Summary of results for: |  |  | February
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2023-02-21 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2023-03-01 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.3 |  | 6.5 - 8.5 |  | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Aluminium | 0.21 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.86 | 10 | 15 | mg/L | No
|  | Total P | 0.132 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.01 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| February | kL |  |  |  | mg/L = milligrams per litre
| Data | 28 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 273
| Maximum | 577
| Mean | 412
| Median | 410
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2023-02-02
| Summary of results for: |  |  | January
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2023-01-24 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2023-02-01 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Aluminium | 0.35 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.94 | 10 | 15 | mg/L | No
|  | Total P | 0.18 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.06 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| January | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 77
| Maximum | 812
| Mean | 418
| Median | 390

## 2022
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2023-01-16
| Summary of results for: |  |  | December
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-12-20 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-12-30 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.4 |  | 6.5 - 8.5 |  | No
|  | TSS | 6 | 15 | 30 | mg/L | No
|  | Aluminium | 0.44 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.75 | 10 | 15 | mg/L | No
|  | Total P | 0.37 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.18 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 341
| Maximum | 632
| Mean | 471
| Median | 506
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2022-01-16
| Summary of results for: |  |  | November
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-11-29 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-12-09 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 11 | 15 | 30 | mg/L | No
|  | Aluminium | 1.12 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.74 | 10 | 15 | mg/L | No
|  | Total P | 0.438 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.45 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 546
| Maximum | 2197
| Mean | 965
| Median | 838
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2022-11-14
| Summary of results for: |  |  | October
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-10-26 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-11-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.4 |  | 6.5 - 8.5 |  | No
|  | TSS | 10 | 15 | 30 | mg/L | No
|  | Aluminium | 0.59 | n/a | n/a | mg/L | No
|  | Faecal coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.88 | 10 | 15 | mg/L | No
|  | Total P | 0.294 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.79 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 358
| Maximum | 856
| Mean | 465.5333
| Median | 415.5
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2022-10-13
| Summary of results for: |  |  | September
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-09-27 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-10-09 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | 8 | 15 | 30 | mg/L | No
|  | Aluminium | 0.44 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.71 | 10 | 15 | mg/L | No
|  | Total P | 0.23 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.17 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 592 | [6 empty] | 30
| Maximum | 1991 | [6 empty] | 592
| Mean | 947 | [6 empty] | 947
| Median | 873 | [6 empty] | 873
| **Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2. | [7 empty] | 1991
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2022-09-16
| Summary of results for: |  |  | August
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-08-31 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-09-09 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| . | pH | 7.3 |  | 6.5 - 8.5 |  | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Aluminium | 0.18 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.37 | 10 | 15 | mg/L | No
|  | Total P | 0.146 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.37 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 622
| Maximum | 1799
| Mean | 879.6333
| Median | 790.5
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-08-12
| Summary of results for: |  |  | July
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-07-27 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-08-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.2 |  | 6.5 - 8.5 |  | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Aluminium | 0.21 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.11 | 10 | 15 | mg/L | No
|  | Total P | 0.152 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.24 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 358
| Maximum | 4387**
| Mean | 1130
| Median | 748
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
|  | Date Data Published: |  |  | 2022-08-12
|  | Summary of results for: |  |  | 2021-22
|  | Number of measurements taken: |  |  | 1
|  | Monitoring frequency required: |  |  | Annual
Sampling Point 3
Environment Monitoring 100 metres upstream of the confluence between the discharge drain and Pipers Flat Creek
|  |  |  | Pollutant | Measurement | Units
|  | Sampled | 2022-07-27 | BOD | <2 | mg/L
|  | Obtained | 2022-08-06 | Oil & Grease | <5 | mg/L
|  |  |  | pH | 7.9
|  |  |  | TSS | 3 | mg/L
|  |  |  | Aluminium | 0.29 | mg/L
|  |  |  | Faecal coliforms | 39 | CFU/100ml
|  |  |  | Total N | 0.44 | mg/L
|  |  |  | Total P | 0.014 | mg/L
|  |  |  | Ammonia | <0.01 | mg/L
|  | Date Data Published: |  |  | 2021-08-12
|  | Summary of results for: |  |  | 2021-22
|  | Number of measurements taken: |  |  | 1
|  | Monitoring frequency required: |  |  | Annual
Sampling Point 4
Environment Monitoring 200 metres downstream of the confluence between the discharge drain and Pipers Flat Creek
|  |  |  | Pollutant | Measurement | Units
|  | Sampled | 2022-07-27 | BOD | <2 | mg/L
|  | Obtained | 2022-08-06 | Oil & Grease | <5 | mg/L
|  |  |  | pH | 7.9
|  |  |  | TSS | 14 | mg/L
|  |  |  | Aluminium | 0.35 | mg/L
|  |  |  | Faecal coliforms | 51 | CFU/100ml
|  |  |  | Total N | 0.47 | mg/L
|  |  |  | Total P | 0.023 | mg/L
|  |  |  | Ammonia | <0.01 | mg/L
| Date Data Published: |  |  | 2022-07-15
| Summary of results for: |  |  | June
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-06-28 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-07-09 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.2 |  | 6.5 - 8.5 |  | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.18 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.54 | 10 | 15 | mg/L | No
|  | Total P | 0.091 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.12 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 390
| Maximum | 949
| Mean | 594
| Median | 534
| Date Data Published: |  |  | 2022-06-15
| Summary of results for: |  |  | May
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-05-24 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-06-03 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.2 |  | 6.5 - 8.5 |  | No
|  | TSS | 3 | 15 | 30 | mg/L | No
|  | Aluminium | 0.13 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.46 | 10 | 15 | mg/L | No
|  | Total P | 0.113 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.03 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 550
| Maximum | 1385**
| Mean | 751
| Median | 674
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-05-11
| Summary of results for: |  |  | April
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-04-26 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-05-09 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.4 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Aluminium | 0.22 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.48 | 10 | 15 | mg/L | No
|  | Total P | 0.171 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.12 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 415
| Mean | 580 |  | 580
| Median | 543.5
| Maximum | 1146
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-04-11
| Summary of results for: |  |  | March
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-03-29 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-04-08 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.4 |  | 6.5 - 8.5 |  | No
|  | TSS | 6 | 15 | 30 | mg/L | No
|  | Aluminium | 3.36 | n/a | n/a | mg/L | No
|  | Faecal coliforms | 4 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.36 | 10 | 15 | mg/L | No
|  | Total P | 0.128 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.13 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 514
| Mean | 930
| Median | 733
| Maximum | 2238**
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-03-07
| Summary of results for: |  |  | February
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-02-22 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-03-03 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 6 | 15 | 30 | mg/L | No
|  | Aluminium | 0.25 | n/a | n/a | mg/L | No
|  | Faecal coliforms | 1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.17 | 10 | 15 | mg/L | No
|  | Total P | 0.134 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.28 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 28 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 386
| Maximum | 1006
| Mean | 626.4286
| Median | 616
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2022-02-03
| Summary of results for: |  |  | January
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedance | Exceedance Comment
Sampled | 2022-01-25 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2022-02-03 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | 2 | 15 | 30 | mg/L | No
|  | Aluminium | 0.16 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.07 | 10 | 15 | mg/L | No
|  | Total P | 0.075 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.06 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 68
| Mean | 799
| Median | 735
| Maximum | 1680**
**Note: High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.

## 2021
Wallerawang Sewage Treatment Plant
| Date Data Published: |  |  | 2021-01-12
| Summary of results for: |  |  | December
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled | 2021-12-21 | BOD | 4 | 10 | 15 | mg/L | No
Result Obtained | 2021-12-30 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 10 | 15 | 30 | mg/L | No
|  | Aluminium | 0.61 | n/a | n/a | mg/L | No
|  | Faecal coliforms | 20 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.97 | 10 | 15 | mg/L | No
|  | Total P | 0.251 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.15 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 398
| Mean | 799.5
| Median | 709
| Maximum | 1648
| Date Data Published: |  |  | 2021-12-09
| Summary of results for: |  |  | November
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled | 2021-11-23 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2021-12-08 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.8 |  | 6.5 - 8.5 |  | No
|  | TSS | 6 | 15 | 30 | mg/L | No
|  | Aluminium | 0.45 | n/a | n/a | mg/L | No
|  | Faecal coliforms | 3 | 200 | 600 | CFU/100ml | No
|  | Total N | 4.62 | 10 | 15 | mg/L | No
|  | Total P | 0.167 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.06 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 366
| Mean | 953.53
| Median | 809.5
| Maximum | 1870
| Date Data Published: |  |  | 2021-11-10
| Summary of results for: |  |  | October
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled | 2021-10-26 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2021-11-06 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Aluminium | 0.16 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 3.54 | 10 | 15 | mg/L | No
|  | Total P | 0.141 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.07 | 2 | 5 | mg/L | No
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 369
| Mean | 551.06
| Median | 523
| Maximum | 1072
| Date Data Published: |  |  | 2021-10-07
| Summary of results for: |  |  | September
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled | 2021-09-28 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2021-10-07 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.4 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Aluminium | 0.31 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 5.53 | 10 | 15 | mg/L | No
|  | Total P | 0.144 | 0.5 | 1 | mg/L | No
|  | Ammonia | 2.44 | 2 | 5 | mg/L | 90th percentile | 90th percentile exceeded for Ammonia. First for this reporting period.
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 443
| Mean | 573
| Median | 560
| Maximum | 1038
| Date Data Published: |  |  | 2021-09-13
| Summary of results for: |  |  | August
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled | 2021-08-31 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained | 2021-09-10 | Oil & Grease | <10 | 5 | 10 | mg/L | No | Oil & Grease reported as <10 mg/L based on technicality (lack of sample volume). 500ml sample bottles were replaced with 2x250ml bottles for sampling. But Sydney water only packed 1x250ml bottle.
|  | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Aluminium | 0.31 | n/a | n/a | mg/L | No
|  | Faecal coliforms | <1 | 200 | 600 | CFU/100ml | No
|  | Total N | 2.78 | 10 | 15 | mg/L | No
|  | Total P | 0.151 | 0.5 | 1 | mg/L | No
|  | Ammonia | 0.24 | 2 | 5 | mg/L
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 425
| Mean | 704
| Median | 546
| Maximum | 1999
Date Data Published: |  |  | 2021-08-10
Summary of results for: |  |  | July
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 27/07/21 | BOD | <2 | 10 | 15 | mg/L | No
Result Obtained 06/08/21 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.4 |  | 6.5 - 8.5 |  | No
| TSS | 4 | 15 | 30 | mg/L | No
| Aluminium | 0.39 | 200 | 600 | mg/L | No
| Faecal coliforms | <1 | 2 | 5 | CFU/100ml | No
| Total N | 2.82 | 0.5 | 1 | mg/L | No
| Total P | 0.133 | 10 | 15 | mg/L | No
| Ammonia | 0.22 | n/a | n/a | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
March | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 394
Mean | 540
Median | 514
Maximum | 889
| Date Data Published: |  |  | 2021-08-10
| Summary of results for: |  |  | 2020-21
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Annual
Sampling Point 3
Environment Monitoring 100 metres upstream of the confluence between the discharge drain and Pipers Flat Creek
|  |  | Pollutant | Measurement | Units
| Sampled | 2021-07-27 | BOD | 2 | mg/L
| Obtained | 2021-08-06 | Oil & Grease | <5 | mg/L
|  |  | pH | 7.7
|  |  | TSS | 5 | mg/L
|  |  | Aluminium | 0.32 | mg/L
|  |  | Faecal coliforms | 46 | CFU/100ml
|  |  | Total N | 0.75 | mg/L
|  |  | Total P | 0.023 | mg/L
|  |  | Ammonia | 0.01 | mg/L
| Date Data Published: |  |  | 2021-08-10
| Summary of results for: |  |  | 2020-21
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Annual
Sampling Point 4
Environment Monitoring 200 metres downstream of the confluence between the discharge drain and Pipers Flat Creek
|  |  | Pollutant | Measurement | Units
| Sampled | 2021-07-27 | BOD | 2 | mg/L
| Obtained | 2021-08-06 | Oil & Grease | <5 | mg/L
|  |  | pH | 7.6
|  |  | TSS | 6 | mg/L
|  |  | Aluminium | 0.35 | mg/L
|  |  | Faecal coliforms | 46 | CFU/100ml
|  |  | Total N | 0.75 | mg/L
|  |  | Total P | 0.029 | mg/L
|  |  | Ammonia | 0.01 | mg/L
| Date Data Published: |  |  | 2021-07-13
| Summary of results for: |  |  | June
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence
| Sampled 29/06/21 | BOD | <2 | 10 | 15 | mg/L | No | Exceedance Comment
| Result Obtained 10/07/21 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.4 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
|  | Ammonia | 0.61 | 2 | 5 | mg/L | No
|  | Total P | 0.178 | 0.5 | 1 | mg/L 90 percentile | No
|  | Total N | 4.43 | 10 | 15 | mg/L | No
|  | Aluminium | 0.48 | n/a | n/a | mg/L
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 351
| Mean | 442.033
| Median | 431
| Maximum | 612
| Date Data Published: |  |  | 2021-06-04
| Summary of results for: |  |  | May
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
| Sampled 25/05/21 | BOD | 3 | 10 | 15 | mg/L | No
| Result Obtained 02/06/21 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.4 |  | 6.5 - 8.5 |  | No
|  | TSS | 5 | 15 | 30 | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
|  | Ammonia | 0.34 | 2 | 5 | mg/L | No
|  | Total P | 0.173 | 0.5 | 1 | mg/L 90 percentile | No
|  | Total N | 4.91 | 10 | 15 | mg/L | No
|  | Aluminium | 0.54 | n/a | n/a | mg/L
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 357
| Mean | 406
| Median | 389
| Maximum | 562
| Date Data Published: |  |  | 2021-05-27
| Summary of results for: |  |  | April
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence
| Sampled 27/04/21 | BOD | <2 | 10 | 15 | mg/L | No | Exceedance Comment
| Result Obtained 26/05/21 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.5 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
|  | Ammonia | 0.18 | 2 | 5 | mg/L | No
|  | Total P | 0.119 | 0.5 | 1 | mg/L 90 percentile | No
|  | Total N | 6.08 | 10 | 15 | mg/L | No
|  | Aluminium | 0.42 | n/a | n/a | mg/L
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 234
| Mean | 423.8
| Median | 406.5
| Maximum | 587
| Date Data Published: |  |  | 2021-04-15
| Summary of results for: |  |  | March
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence
| Sampled 30/03/21 | BOD | <2 | 10 | 15 | mg/L | No | Exceedance Comment
| Result Obtained 10/04/21 | Oil & Grease | <5 | 5 | 10 | mg/L | No
|  | pH | 7.6 |  | 6.5 - 8.5 |  | No
|  | TSS | 4 | 15 | 30 | mg/L | No
|  | Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
|  | Ammonia | 0.66 | 2 | 5 | mg/L | No
|  | Total P | 0.124 | 0.5 | 1 | mg/L 90 percentile | No
|  | Total N | 3.76 | 10 | 15 | mg/L | No
|  | Aluminium | 0.45 | n/a | n/a | mg/L
| Point 1 |  |  |  |  | Summary of Units of Measure
| Month | Volume Discharged
| March | kL |  |  |  | mg/L = milligrams per litre
| Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Minimum | 313
| Mean | 742.74
| Median | 596
| Maximum | 2408**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
| Date Data Published: |  |  | 2021-03-17
| Summary of results for: |  |  | February
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598 |  | Units | Exceedence | Exceedance Comment
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | mg/L | No
| Sampled 23/02/21 | BOD | 3 | 10 | 15 | mg/L | No
| Obtained 11/03/21 | Oil & Grease | <5 | 5 | 10 |  | No
|  | pH | 7.9 |  | 6.5 - 8.5 | mg/L | No
|  | TSS | 5 | 15 | 30 | cfu/100mL | No
|  | Faecal Coliforms | 15 | 200 | 600 | mg/L | No
|  | Ammonia | 0.41 | 2 | 5 | mg/L 90 percentile | No
|  | Total P | 0.213 | 0.5 | 1 | mg/L | No
|  | Total N | 4.32 | 10 | 15 | mg/L
|  | Aluminium | 0.44
Summary of Units of Measure
Point 1
| Month | Volume Discharged |  |  |  | mg/L = milligrams per litre
| February | kL |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Data | 28
| Minimum | 335
| Mean | 458
| Median | 421
| Maximum | 932
| Date Data Published: |  |  | 2021-02-22
| Summary of results for: |  |  | January
| Number of measurements taken: |  |  | 1
| Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
| Licensee: Lithgow City Council |  |  | EPL no. 598 |  | Units | Exceedence
|  | Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | mg/L | No
| Sampled 27/01/21 | BOD | 2 | 10 | 15 | mg/L | No
| Obtained 10/02/21 | Oil & Grease | <5 | 5 | 10 |  | No
|  | pH | 7.7 |  | 6.5 - 8.5 | mg/L | No
|  | TSS | 3 | 15 | 30 | cfu/100mL | No
|  | Faecal Coliforms | <1 | 200 | 600 | mg/L | No
|  | Ammonia | 0.57 | 2 | 5 | mg/L 90 percentile | No
|  | Total P | 0.189 | 0.5 | 1 | mg/L | No
|  | Total N | 4.48 | 10 | 15 | mg/L
|  | Aluminium | 0.39
Summary of Units of Measure
Point 1
| Month | Volume Discharged |  |  |  | mg/L = milligrams per litre
| January | kL |  |  |  | CFU/100mL = colony forming units per 100 millitres
| Data | 31
| Minimum | 333
| Mean | 512
| Median | 417
| Maximum | 1,214**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.

## 2020
Wallerawang Sewage Treatment Plant
Date Data Published: |  |  | 2021-01-18
Summary of results for: |  |  | December
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 16/12/20 | BOD | 4 | 10 | 15 | mg/L | No
Obtained 11/01/21 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 8.4 |  | 6.5 - 8.5 |  | No
| TSS | 13 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.19 | 2 | 5 | mg/L | No
| Total P | 0.377 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 7.89 | 10 | 15 | mg/L | No
| Aluminium | 1.69 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
December | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 287
Mean | 471
Median | 419
Maximum | 884
Date Data Published: |  |  | 2020-12-22
Summary of results for: |  |  | November
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 24/11/20 | BOD | 6 | 10 | 15 | mg/L | No
Obtained 14/12/20 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 8.4 |  | 6.5 - 8.5 |  | No
| TSS | 18 | 15 | 30 | mg/L | No
| Faecal Coliforms | 14 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.96 | 2 | 5 | mg/L | No
| Total P | 1.16 | 0.5 | 1 | mg/L 90 percentile | Yes | The result does not correlate with Council site sampling and on further analysis, it appears that there may have been an error recording the result in the laboratory. A retest of the sample is being undertaken. The results will be amended when the retesting is complete. 18/01/2021 - Retesting by Sydney Water Analytical returned the same results. Subsequent testing in December, returned compliant results that were within 5% of our results. The high reading in November and the discrepancy with our analysis, remain undetermined. This could have been a result of the operator sampling a slug of higher concentration effluent or interference from contamination in the chlorine contact tank.
| Total N | 5.15 | 10 | 15 | mg/L | No
| Aluminium | 1.25 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
November | kL |  |  |  | mg/L = milligrams per litre
Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 415
Mean | 550
Median | 507
Maximum | 874
Date Data Published: |  |  | 2020-11-17
Summary of results for: |  |  | October
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 27/10/20 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 06/11/20 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.8 |  | 6.5 - 8.5 |  | No
| TSS | 8 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.51 | 2 | 5 | mg/L | No
| Total P | 0.24 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 4.74 | 10 | 15 | mg/L | No
| Aluminium | 0.73 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
October | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 351
Mean | 508
Median | 471
Maximum | 1,066**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2019-10-13
Summary of results for: |  |  | 2020-21
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 3
Environment Monitoring 100 metres upstream of the confluence between the discharge drain and Pipers Flat Creek
|  | Pollutant | Measurement | Units
Sampled | 2020-09-29 | BOD | <2 | mg/L
Obtained | 2020-10-08 | Oil & Grease | <5 | mg/L
|  | pH | 7.6
|  | TSS | <2 | mg/L
|  | Faecal Coliforms | 55 | cfu/100mL
|  | Ammonia | 0.01 | mg/L
|  | Total P | 0.013 | mg/L
|  | Total N | 0.67 | mg/L
|  | Aluminium | 0.11 | mg/L
Date Data Published: |  |  | 2019-10-13
Summary of results for: |  |  | 2020-21
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 4
Environment Monitoring 200 metres downstream of the confluence between the discharge drain and Pipers Flat Creek
|  | Pollutant | Measurement | Units
Sampled | 2020-09-29 | BOD | <2 | mg/L
Obtained | 2020-10-08 | Oil & Grease | <5 | mg/L
|  | pH | 7.6
|  | TSS | 5 | mg/L
|  | Faecal Coliforms | ~72 | cfu/100mL
|  | Ammonia | 0.03 | mg/L
|  | Total P | 0.03 | mg/L
|  | Total N | 0.8 | mg/L
|  | Aluminium | 0.25 | mg/L
Date Data Published: |  |  | 2020-10-13
Summary of results for: |  |  | September
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 29/09/20 | BOD | 5 | 10 | 15 | mg/L | No
Obtained 08/10/20 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.6 |  | 6.5 - 8.5 |  | No
| TSS | 9 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.16 | 2 | 5 | mg/L | No
| Total P | 0.314 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 7.66 | 10 | 15 | mg/L | No
| Aluminium | 0.57 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
September | kL |  |  |  | mg/L = milligrams per litre
Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 494
Mean | 642
Median | 602
Maximum | 1,046**
**Rain gauge within the catchment of Wallerawang recorded 16.8mm on 23/09/2020. This wet weather event caused the maximum volume dicharged to exceed the licence limit.
Date Data Published: |  |  | 2020-09-09
Summary of results for: |  |  | August
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 25/08/20 | BOD | 4 | 10 | 15 | mg/L | No
Obtained 04/09/20 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.3 |  | 6.5 - 8.5 |  | No
| TSS | 11 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.44 | 2 | 5 | mg/L | No
| Total P | 0.365 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 6.52 | 10 | 15 | mg/L | No
| Aluminium | 0.63 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
August | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 568
Mean | 1012
Median | 919
Maximum | 1,900**
**Note. There were four periods in the month of August where rainfall exceeded 15mm in a 24hr period. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-08-12
Summary of results for: |  |  | July
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled - | BOD |  | 10 | 15 | mg/L |  | No samples taken for July 2020.
Obtained 11/08/20 | Oil & Grease |  | 5 | 10 | mg/L
| pH |  |  | 6.5 - 8.5
| TSS |  | 15 | 30 | mg/L
| Faecal Coliforms |  | 200 | 600 | cfu/100mL
| Ammonia |  | 2 | 5 | mg/L
| Total P |  | 0.5 | 1 | mg/L 90 percentile
| Total N |  | 10 | 15 | mg/L
| Aluminium |  |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
July | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 379
Mean | 582
Median | 439
Maximum | 1,928**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-07-16
Summary of results for: |  |  | June
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 23/06/20 | BOD | 9 | 10 | 15 | mg/L | No
Obtained 16/07/20 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.6 |  | 6.5 - 8.5 |  | No
| TSS | 8 | 15 | 30 | mg/L | No
| Faecal Coliforms | 3 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.33 | 2 | 5 | mg/L | No
| Total P | 0.49 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 7.62 | 10 | 15 | mg/L | No
| Aluminium | 0.31 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
June | kL |  |  |  | mg/L = milligrams per litre
Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 221
Mean | 455
Median | 439
Maximum | 755
Date Data Published: |  |  | 2020-06-11
Summary of results for: |  |  | May
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 27/05/20 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 04/06/20 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.3 |  | 6.5 - 8.5 |  | No
| TSS | 5 | 15 | 30 | mg/L | No
| Faecal Coliforms | 15 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.23 | 2 | 5 | mg/L | No
| Total P | 0.233 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 16.8 | 10 | 15 | mg/L | Yes | Failed non-return valve was allowing WAS to return into the IDEA Tank.
| Aluminium | 0.39 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
May | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 346
Mean | 532
Median | 479
Maximum | 1,319**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-05-19
Summary of results for: |  |  | April
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 28/04/20 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 06/05/20 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.6 |  | 6.5 - 8.5 |  | No
| TSS | 2 | 15 | 30 | mg/L | No
| Faecal Coliforms | 4 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.2 | 2 | 5 | mg/L | No
| Total P | 0.373 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 7.38 | 10 | 15 | mg/L | No
| Aluminium | 0.18 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
April | kL |  |  |  | mg/L = milligrams per litre
Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 364
Mean | 518
Median | 445
Maximum | 1,319**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-04-17
Summary of results for: |  |  | March
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 25/03/20 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 03/04/20 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 6.6 |  | 6.5 - 8.5 |  | No
| TSS | 5 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 1.29 | 2 | 5 | mg/L | No
| Total P | 0.1 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 12.3 | 10 | 15 | mg/L | No
| Aluminium | 0.13 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
March | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 312
Mean | 475
Median | 424
Maximum | 1,065**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-03-19
Summary of results for: |  |  | February
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 26/02/20 | BOD | 2 | 10 | 15 | mg/L | No
Obtained 06/03/20 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.5 |  | 6.5 - 8.5 |  | No
| TSS | 4 | 15 | 30 | mg/L | No
| Faecal Coliforms | ~87 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.42 | 2 | 5 | mg/L | No
| Total P | 0.442 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 14.6 | 10 | 15 | mg/L | No
| Aluminium | 0.16 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
February | kL |  |  |  | mg/L = milligrams per litre
Data | 29 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 309
Mean | 452
Median | 390
Maximum | 1,316**
**Note. High flow was recorded due to wet weather. This is in accordance with Condition L4 4.2.
Date Data Published: |  |  | 2020-02-25
Summary of results for: |  |  | January
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 29/01/20 | BOD | 10 | 10 | 15 | mg/L | No
Obtained 12/02/20 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 6.9 |  | 6.5 - 8.5 |  | No
| TSS | 20 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 6.61 | 2 | 5 | mg/L | Yes | Council has experienced issues with Dissolved Oxygen (DO) set points. New DO sensor have been installed and SCADA control improved to ensure adequate aeration is achieved for nitrification to occur.
| Total P | 0.52 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 14 | 10 | 15 | mg/L | No
| Aluminium | 1.83 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
January | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 140
Mean | 330
Median | 331
Maximum | 616

## 2019
Wallerawang Sewage Treatment Plant
Date Data Published: |  |  | 2020-01-08
Summary of results for: |  |  | December
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 18/12/19 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 06/01/20 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.3 |  | 6.5 - 8.5 |  | No
| TSS | 3 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | <0.01 | 2 | 5 | mg/L | No
| Total P | 0.096 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 4.74 | 10 | 15 | mg/L | No
| Aluminium | 0.23 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
December | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 224
Mean | 320
Median | 339
Maximum | 414
Date Data Published: |  |  | 2019-12-09
Summary of results for: |  |  | November
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 27/11/19 | BOD | 3 | 10 | 15 | mg/L | No
Obtained 4/12/19 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 6.5 |  | 6.5 - 8.5 |  | No
| TSS | 4 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.01 | 2 | 5 | mg/L | No
| Total P | 0.249 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 6.24 | 10 | 15 | mg/L | No
| Aluminium | 0.99 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
October | kL |  |  |  | mg/L = milligrams per litre
Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 254
Mean | 363
Median | 366
Maximum | 468
Date Data Published: |  |  | 2019-11-13
Summary of results for: |  |  | 2019-20
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 3
Environment Monitoring 100 metres upstream of Point 1
|  | Pollutant | Measurement | Units
Sampled 29/10/19 |  | BOD | 7 | mg/L
Obtained 12/11/19 |  | Oil & Grease | <5 | mg/L
|  | pH | 8.5
|  | TSS | 95 | mg/L
|  | Faecal Coliforms | ~37 | cfu/100mL
|  | Ammonia | 0.01 | mg/L
|  | Total P | 0.355 | mg/L
|  | Total N | 2.2 | mg/L
|  | Aluminium | 4.1 | mg/L
Date Data Published: |  |  | 2019-11-13
Summary of results for: |  |  | 2019-20
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 4
Environment Monitoring 200 metres downstream of Point 1
|  | Pollutant | Measurement | Units
Sampled 29/10/19 |  | BOD | <2 | mg/L
Obtained 12/11/19 |  | Oil & Grease | <5 | mg/L
|  | pH | 6.9
|  | TSS | 9 | mg/L
|  | Faecal Coliforms | <1 | cfu/100mL
|  | Ammonia | 0.99 | mg/L
|  | Total P | 0.172 | mg/L
|  | Total N | 11.7 | mg/L
Date Data Published: |  |  | 2019-11-13
Summary of results for: |  |  | October
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 29/10/19 | BOD | <2 | 10 | 15 | mg/L | No
Obtained 12/11/19 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 6.5 |  | 6.5 - 8.5 |  | No
| TSS | 4 | 15 | 30 | mg/L | No
| Faecal Coliforms | <1 | 200 | 600 | cfu/100mL | No
| Ammonia | 0.01 | 2 | 5 | mg/L | No
| Total P | 0.179 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 13.2 | 10 | 15 | mg/L | No
| Aluminium | 0.26 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
October | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 296
Mean | 377
Median | 375
Maximum | 458
Date Data Published: |  |  | 2019-10-21
Summary of results for: |  |  | September
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
Sampled 25/09/19 | BOD | 5 | 10 | 15 | mg/L | No
Obtained 03/10/19 | Oil & Grease | <5 | 5 | 10 | mg/L | No
| pH | 7.6 |  | 6.5 - 8.5 |  | No
| TSS | 8 | 15 | 30 | mg/L | No
| Faecal Coliforms | 7 | 200 | 600 | cfu/100mL | No
| Ammonia | 1.39 | 2 | 5 | mg/L | No
| Total P | 0.271 | 0.5 | 1 | mg/L 90 percentile | No
| Total N | 13.8 | 10 | 15 | mg/L | No
| Aluminium | 0.61 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
September | kL |  |  |  | mg/L = milligrams per litre
Data | 13** |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 256
Mean | 428
Median | 449
Maximum | 524
**Note. Discharge to the environment occured for a total of 13 days in September 2019 (18/09/19 - 30/09/19).
Date Data Published: |  |  | 2019-09-11
Summary of results for: |  |  | August
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
| BOD |  | 10 | 15 | mg/L | No | Plant was not discharging to the environment at the time of routine sample. Discharge to the environment occurred 7 August to 18 August 2019. On the remaining dates in August, the plant was discharging to storage lagoons. Discharging to the storage lagoons was undertaken while adjustments were being made to ensure licence limits would not be breached. This is in accordance with Condition O - 4.2 of the Licence.
| Oil & Grease |  | 5 | 10 | mg/L | No
| pH |  |  | 6.5 - 8.5 |  | No
| TSS |  | 15 | 30 | mg/L | No
| Faecal Coliforms |  | 200 | 600 | cfu/100mL | No
| Ammonia |  | 2 | 5 | mg/L | No
| Total P |  | 0.5 | 1 | mg/L 90 percentile | No
| Total N |  | 10 | 15 | mg/L | No
| Aluminium |  |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
August | kL |  |  |  | mg/L = milligrams per litre
Data | 13** |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 322
Mean | 394
Median | 394
Maximum | 472
**Note. Volume discharge results have been amended to reflect the dates the plant was discharging to the environment.
Date Data Published: |  |  | 2019-08-13
Summary of results for: |  |  | July
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | 90th Percentile Limit | 100th Percentile Limit | Units | Exceedence | Exceedance Comment
| BOD |  | 10 | 15 | mg/L | No | Plant was not discharging to the environment at the time of routine sample. Discharge to the environment occurred 2 July to 28 July 2019. On the remaining dates in July, the plant was discharging to storage lagoons. Discharging to the storage lagoons was undertaken while adjustments were being made to ensure licence limits would not be breached. This is in accordance with Condition O - 4.2 of the Licence.
| Oil & Grease |  | 5 | 10 | mg/L | No
| pH |  |  | 6.5 - 8.5 |  | No
| TSS |  | 15 | 30 | mg/L | No
| Faecal Coliforms |  | 200 | 600 | cfu/100mL | No
| Ammonia |  | 2 | 5 | mg/L | No
| Total P |  | 0.5 | 1 | mg/L 90 percentile | No
| Total N |  | 10 | 15 | mg/L | No
| Aluminium |  |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
July | kL |  |  |  | mg/L = milligrams per litre
Data | 27** |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 307
Mean | 383
Median | 389
Maximum | 458
**Note. Volume discharge results have been amended to reflect the dates the plant was discharging to the environment.
Date Data Published: |  |  | 2019-07-23
Summary of results for: |  |  | June
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | Limit |  | Units | Exceedence | Exceedance Comment
| BOD |  | 10 |  | mg/L | No | Plant was not discharging to the environment at the time of sample. Discharging to the storage lagoons occurred while adjustments were being made to ensure licence limits would not be breached. This is in accordance with Condition O - 4.2 of the Licence.
| Oil & Grease |  | 10 |  | mg/L | No
| pH |  | 6.5 - 8.5 |  |  | No
| TSS |  | 15 |  | mg/L | No
| Faecal Coliforms |  | 200 |  | cfu/100mL | No
| Ammonia |  | 2 |  | mg/L | No
| Total P |  | 0.5 |  | mg/L 90 percentile | No
| Total N |  | 10 |  | mg/L | No
| Aluminium |  |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
June | kL |  |  |  | mg/L = milligrams per litre
Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 309
Mean | 399
Median | 403
Maximum | 465
Date Data Published: |  |  | 2019-06-17
Summary of results for: |  |  | May
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | Limit |  | Units | Exceedence | Exceedance Comment
Sampled 29/05/2019 | BOD | <2 | 10 |  | mg/L | No
Obtained 08/06/2019 | Oil & Grease | <5 | 10 |  | mg/L | No
| pH | 7.5 | 6.5 - 8.5 |  |  | No
| TSS | 7 | 15 |  | mg/L | No
| Faecal Coliforms | 2 | 200 |  | cfu/100mL | No
| Ammonia | 2.79 | 2 |  | mg/L | Yes | A combination of the aeration cycle and the seasonal change has affected the process of de-nitrafication.
| Total P | 0.143 | 0.5 |  | mg/L 90 percentile | No
| Total N | 7.32 | 10 |  | mg/L | No
| Aluminium | 0.65 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
May | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 246
Mean | 406
Median | 389
Maximum | 677
Correction Log - Aluminium results not previously recorded, previous reports amended with results.
Date Data Published: |  |  | 2019-05-14
Summary of results for: |  |  | April
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | Limit |  | Units | Exceedence | Exceedance Comment
Sampled 23/04/19 | BOD | <2 | 10 |  | mg/L | No
Obtained 06/05/19 | Oil & Grease | <5 | 10 |  | mg/L | No
| pH | 7.5 | 6.5 - 8.5 |  |  | No
| TSS | 6 | 15 |  | mg/L | No
| Faecal Coliforms | ~65 | 200 |  | cfu/100mL | No
| Ammonia | 1.06 | 2 |  | mg/L | No
| Total P | 0.115 | 0.5 |  | mg/L 90 percentile | No
| Total N | 12.7 | 10 |  | mg/L | Yes | In April, adjustments were made slowly to counter the temperature fluctuations. Further testing by staff will be undertaken throughout May to ensure correct testing practice.
| Aluminium | 0.75 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
April | kL |  |  |  | mg/L = milligrams per litre
Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 279
Mean | 384
Median | 392
Maximum | 497
Date Data Published: |  |  | 2019-04-15
Summary of results for: |  |  | March
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | Limit |  | Units | Exceedence | Exceedance Comment
Sampled 26/03/19 | BOD | <2 | 10 |  | mg/L | No
Obtained 8/04/19 | Oil & Grease | <5 | 10 |  | mg/L | No
| pH | 7.4 | 6.5 - 8.5 |  |  | No
| TSS | 5 | 15 |  | mg/L | No
| Faecal Coliforms | 37 | 200 |  | cfu/100mL | No
| Ammonia | 0.3 | 2 |  | mg/L | No
| Total P | 0.12 | 0.5 |  | mg/L 90 percentile | No
| Total N | 10.4 | 10 |  | mg/L | Yes | The exceedance is the result of the rapid cooling of the weather at night, which has resulted in fluctuations in the treatment process. Aeration cycles have been adjusted to combat this.
| Aluminium | 0.46 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
March | kL |  |  |  | mg/L = milligrams per litre
Data | 31 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 279
Mean | 430
Median | 417
Maximum | 987
Date Data Published: |  |  | 2019-03-14
Summary of results for: |  |  | February
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | Limit |  | Units | Exceedence | Exceedance Comment
Sampled 26/02/19 | BOD | <2 | 10 |  | mg/L | No
Obtained 8/03/19 | Oil & Grease | <5 | 10 |  | mg/L | No
| pH | 7.2 | 6.5 - 8.5 |  |  | No
| TSS | 6 | 15 |  | mg/L | No
| Faecal Coliforms | <1 | 200 |  | cfu/100mL | No
| Ammonia | 0.05 | 2 |  | mg/L | No
| Total P | 0.144 | 0.5 |  | mg/L 90 percentile | No
| Total N | 8.3 | 10 |  | mg/L | No
| Aluminium | 0.61 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
February | kL |  |  |  | mg/L = milligrams per litre
Data | 28 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 288
Mean | 411
Median | 412
Maximum | 543
Date Data Published: |  |  | 2019-02-07
Summary of results for: |  |  | January
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | Limit |  | Units | Exceedence | Exceedance Comment
Sampled 29/01/19 | BOD | <2 | 10 |  | mg/L | No
Obtained 6/02/19 | Oil & Grease | <5 | 10 |  | mg/L | No
| pH | 7.3 | 6.5 - 8.5 |  |  | No
| TSS | 7 | 15 |  | mg/L | No
| Faecal Coliforms | <1 | 200 |  | cfu/100mL | No
| Ammonia | 0.2 | 2 |  | mg/L | No
| Total P | 0.135 | 0.5 |  | mg/L 90 percentile | No
| Total N | 6.24 | 10 |  | mg/L | No
| Aluminium | 0.7 |  |  | mg/L
Point 1 |  |  |  |  | Summary of Units of Measure
Month | Volume Discharged
January | kL |  |  |  | mg/L = milligrams per litre
Data | 30 |  |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 31
Mean | 487
Median | 479
Maximum | 910

## 2018
Wallerawang Sewage Treatment Plant
Date Data Published: |  |  | 2019-01-10
Summary of results for: |  |  | December
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 18/12/18 | BOD | <2 | 10 | mg/L | No
Obtained 5/01/19 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7 | 6.5 - 8.5 |  | No
| TSS | 6 | 15 | mg/L | No
| Faecal Coliforms | <1 | 200 | cfu/100mL | No
| Ammonia | 0.01 | 2 | mg/L | No
| Total P | 0.126 | 0.5 | mg/L 90 percentile | No
| Total N | 5.55 | 10 | mg/L | No
| Aluminium | 0.58 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
December | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 288
Mean | 469
Median | 445
Maximum | 983
Date Data Published: |  |  | 2018-12-07
Summary of results for: |  |  | November
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 27/11/18 | BOD | <2 | 10 | mg/L | No
Obtained 6/12/18 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7 | 6.5 - 8.5 |  | No
| TSS | 7 | 15 | mg/L | No
| Faecal Coliforms | <1 | 200 | cfu/100mL | No
| Ammonia | <0.01 | 2 | mg/L | No
| Total P | 0.192 | 0.5 | mg/L 90 percentile | No
| Total N | 6.51 | 10 | mg/L | No
| Aluminium | 0.59 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
November | kL |  |  | mg/L = milligrams per litre
Data | 30 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 186
Mean | 416
Median | 397
Maximum | 917
Date Data Published: |  |  | 2018-11-12
Summary of results for: |  |  | October
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Monthly
Sample Point 1
Discharge to Pipers Flat/Adams Creek
Licensee: Lithgow City Council |  |  | EPL no. 598
| Pollutant | Measurement | Limit | Units | Exceedence | Exceedance Comment
Sampled 30/10/18 | BOD | <2 | 10 | mg/L | No
Obtained 10/11/18 | Oil & Grease | <5 | 10 | mg/L | No
| pH | 7.1 | 6.5 - 8.5 |  | No
| TSS | 4 | 15 | mg/L | No
| Faecal Coliforms | <1 | 200 | cfu/100mL | No
| Ammonia | <0.01 | 2 | mg/L | No
| Total P | 0.118 | 0.5 | mg/L 90 percentile | No
| Total N | 9.08 | 10 | mg/L | No
| Aluminium | 0.35 |  | mg/L
Point 1 |  |  |  | Summary of Units of Measure
Month | Volume Discharged
October | kL |  |  | mg/L = milligrams per litre
Data | 31 |  |  | CFU/100mL = colony forming units per 100 millitres
Minimum | 81
Mean | 491
Median | 464
Maximum | 845
Date Data Published: |  |  | 2018-11-12
Summary of results for: |  |  | 2018-19
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 3
Environment Monitoring 100 metres upstream of Point 1
|  | Pollutant | Measurement | Units
Sampled 28/08/18 |  | BOD | <2 | mg/L
Obtained 5/09/18 |  | Oil & Grease | <5 | mg/L
|  | pH | 7.7
|  | TSS | 58 | mg/L
|  | Faecal Coliforms | 91 | cfu/100mL
|  | Ammonia | 0.01 | mg/L
|  | Total P | 0.071 | mg/L
|  | Total N | 0.67 | mg/L
Date Data Published: |  |  | 2018-11-12
Summary of results for: |  |  | 2018-19
Number of measurements taken: |  |  | 1
Monitoring frequency required: |  |  | Annual
Sampling Point 4
Environment Monitoring 200 metres downstream of Point 1
|  | Pollutant | Measurement | Units
Sampled 28/08/18 |  | BOD | <2 | mg/L
Obtained 5/09/18 |  | Oil & Grease | <5 | mg/L
|  | pH | 7.6
|  | TSS | 5 | mg/L
|  | Faecal Coliforms | 130 | cfu/100mL
|  | Ammonia | 0.15 | mg/L
|  | Total P | 0.046 | mg/L
|  | Total N | 0.82 | mg/L
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled |  | BOD | ** | 10 | mg/L | 1 |  |  |  | No
Obtained |  | Oil & Grease | ** | 10 | mg/L | 1 |  |  |  | No
Published | 2018-10-08 | pH | ** | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | ** | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | ** | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | ** | 2 | mg/L | 1 |  |  |  | No
|  | Total N | ** | 10 | mg/L | 1 |  |  |  | No
|  | Total P | ** | 0.5 | mg/L | 1 |  |  |  | No
** No samples taken, as during the sampling period, Council was discharging to the holding lagoons.
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 30 | 290 | 888 | 472 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-08-28 | BOD | 4 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2018-09-06 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2018-09-07 | pH | 7.2 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 11 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.72 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 5.89 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.344 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.71 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 321 | 674 | 466 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-07-24 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2018-08-01 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2018-08-15 | pH | 7.2 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 4 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 1.23 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 6.74 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.176 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.24 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 149 | 434 | 340 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-06-26 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2018-07-04 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2018-07-09 | pH | 7.4 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 12 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 25.1 | 2 | mg/L | 1 |  |  |  | Yes
|  | Total N | 26.6 | 10 | mg/L | 1 |  |  |  | Yes
|  | Total P | 0.268 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.98 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 30 | 318 | 508 | 424 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-05-29 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2018-06-07 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2018-06-13 | pH | 7.4 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 7 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 6.7 | 2 | mg/L | 1 |  |  |  | Yes
|  | Total N | 9.14 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.205 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.68 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 230 | 491 | 401 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-04-17 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2018-04-27 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2018-05-16 | pH | 6.7 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 12 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | <0.01 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 5.87 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.425 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 2.93 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 30 |  |  |  | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-03-28 | BOD | 4 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2018-04-07 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2018-04-13 | pH | 7.4 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 3 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | <0.01 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 6.79 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.145 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.17 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 134 | 549 | 402 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-02-27 | BOD | 2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2018-03-10 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2018-03-16 | pH | 7.3 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 4 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.62 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 5.18 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 1.04 | 0.5 | mg/L | 1 |  |  |  | Yes
|  | Aluminium | 0.38 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 28 | 276 | 632 | 422 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-01-30 | BOD | 3 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-02-08 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2018-02-16 | pH | 7.6 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 3 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | <0.01 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 10 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.13 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.55 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 219 | 560 | 358 | No

## 2017
Wallerawang Sewage Treatment Plant
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-12-20 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-12-30 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2018-01-11 | pH | 7.7 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 4 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | <0.01 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 5.63 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.156 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.7 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 264 | 693 | 434 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-11-28 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-12-12 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-12-15 | pH | 7.7 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 8 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | 300 | 200 | cfu/100mL | 1 |  |  |  | Yes
|  | Ammonia as N | 0.37 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 7.83 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.171 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.63 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 30 | 236 | 480 | 371 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-10-24 | BOD | 9 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-11-04 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-11-07 | pH | 7.8 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 8 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.01 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 2.86 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.23 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.92 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 299 | 1060 | 377 | Yes
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-09-27 | BOD | 5 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-10-06 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-10-10 | pH | 7.8 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 6 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.01 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 4.79 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.27 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 1.22 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 30 | 296 | 374 | 333 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-08-29 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-09-11 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-09-12 | pH | 7.8 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 11 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.17 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 9.45 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.35 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 1.72 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 324 | 454 | 364 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-07-26 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-08-04 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-08-14 | pH | 7.6 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 6 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.87 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 8.68 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.241 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.84 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 276 | 426 | 339 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-06-27 | BOD | 3 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-07-05 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-07-10 | pH | 7.65 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.11 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 2.69 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.22 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.8 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 30 | 316 | 428 | 349 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-05-24 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-05-30 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-06-09 | pH | 7.4 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.05 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 4.4 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.18 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.69 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 316 | 615 | 347 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-04-18 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-04-27 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-05-08 | pH | 8 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <2 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.05 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 9.2 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.1 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.43 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 30 | 311 | 415 | 349 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-03-22 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-03-30 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-04-07 | pH | 6.1 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <2 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 2.75 | 2 | mg/L | 1 |  |  |  | Yes
|  | Total N | 6.4 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.22 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.47 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 329 | 873 | 433 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-02-21 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-03-07 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-03-14 | pH | 7.5 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | 70 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.5 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 1.4 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.08 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.42 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 28 | 293 | 364 | 326 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-01-18 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-01-31 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-02-14 | pH | 7.76 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | 1400 | 200 | cfu/100mL | 1 |  |  |  | Yes
|  | Ammonia as N | 0.09 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 2.59 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.13 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.48 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 301 | 456 | 334 | No

## 2016
Wallerawang Sewage Treatment Plant
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-12-20 | BOD | 3 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2017-01-03 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2017-01-16 | pH | 7.79 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 6 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | 140 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 7.64 | 2 | mg/L | 1 |  |  |  | Yes
|  | Total N | 9.07 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.13 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.38 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 319 | 1151 | 405 | Yes
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-11-15 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-11-23 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2016-12-15 | pH | 7.86 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | 33 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.4 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 6 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.14 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.46 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 30 | 340 | 1010 | 444 | Yes
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-10-18 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-11-01 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2016-11-11 | pH | 7.85 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | 6 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.35 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 6.5 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.06 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.29 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 412 | 733 | 537 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-09-20 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-10-20 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2016-11-01 | pH | 7.8 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.17 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 5 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.15 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.64 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 30 | 599 | 2368 | 936 | Yes
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-08-23 | BOD | 4 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-08-31 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2016-09-12 | pH | 7.85 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | 3 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.61 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 2.3 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.34 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.57 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 486 | 1148 | 661 | Yes
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-07-26 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-08-03 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2016-08-12 | pH | 8.3 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | 2 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.28 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 6.4 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.14 | 0.5 | mg/L | 1 |  |  |  | No
|  | Aluminium | 0.49 |  | mg/L | 1
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 456 | 2349 | 766 | Yes
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-06-28 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-07-09 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2016-07-21 | pH | 8 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 1.6 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 7.41 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.184 | 0.5 | mg/L | 1 |  |  |  | No
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 30 | 324 | 1184 | 657 | Yes
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-05-24 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-06-06 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2016-06-14 | pH | 8.2 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 5 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.1 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 5.23 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.199 | 0.5 | mg/L | 1 |  |  |  | No
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 301 | 449 | 353 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-04-26 | BOD | 2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-05-06 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2016-05-10 | pH | 8 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 4 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | 0.2 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 10.5 | 10 | mg/L | 1 |  |  |  | Yes
|  | Total P | 0.211 | 0.5 | mg/L | 1 |  |  |  | No
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 30 | 299 | 400 | 344 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-03-29 | BOD | 9 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-04-13 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2016-04-21 | pH | 8 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 3 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | 52 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | <0.1 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 6.05 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.179 | 0.5 | mg/L | 1 |  |  |  | No
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 326 | 845 | 411 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-02-23 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-03-16 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2016-03-22 | pH | 7.2 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | <2 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | <0.1 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 3.72 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.132 | 0.5 | mg/L | 1 |  |  |  | No
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 29 | 308 | 603 | 374 | No
Sampling point: 1 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-01-19 | BOD | <2 | 10 | mg/L | 1 |  |  |  | No
Obtained | 2016-02-01 | Oil & Grease | <5 | 10 | mg/L | 1 |  |  |  | No
Published | 2016-02-05 | pH | 7.4 | 6.5-8.5 |  | 1 |  |  |  | No
|  | TSS | 7 | 15 | mg/L | 1 |  |  |  | No
|  | Faecal Coliforms | <1 | 200 | cfu/100mL | 1 |  |  |  | No
|  | Ammonia as N | <0.1 | 2 | mg/L | 1 |  |  |  | No
|  | Total N | 3.8 | 10 | mg/L | 1 |  |  |  | No
|  | Total P | 0.215 | 0.5 | mg/L | 1 |  |  |  | No
Sampling point: 3 |  |  | EPL no. 598 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
|  | Daily Flow |  | 1000 | kL/day | 31 | 269 | 827 | 404 | No