## 2025
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
February |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2025-02-26 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2025-03-05 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2025-03-07 | Aluminium | 0.18 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 28 | 166 | 822 | 414
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
March |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2025-03-25 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2025-03-26 | TSS | 3 | 30 | mg/L |  |  |  |  | No
Published | 2025-04-03 | Aluminium | 0.17 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 68 | 853 | 372

## 2024
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
November |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2025-01-29 | pH | 7.3 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2025-02-05 | TSS | 3 | 30 | mg/L |  |  |  |  | No
Published | 2025-02-10 | Aluminium | 0.2 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 161 | 778 | 303
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
November |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2024-11-26 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2024-12-06 | TSS | 3 | 30 | mg/L |  |  |  |  | No
Published | 2024-12-06 | Aluminium | 0.39 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 87 | 792 | 359
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
October |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2024-10-29 | pH | 7.3 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2024-11-06 | TSS | 11 | 30 | mg/L |  |  |  |  | No
Published | 2024-11-08 | Aluminium | 1.18 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 11 | 351 | 968 | 487
|  | Comments: | Clarifier sludge removal process took place in this month.
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
September |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2024-09-24 | pH | 7.3 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2024-10-03 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2024-10-08 | Aluminium | 0.68 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 263 | 527 | 400
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
August |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2024-08-27 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2024-09-10 | TSS | 8 | 30 | mg/L |  |  |  |  | No
Published | 2024-09-12 | Aluminium | 1.83 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 175 | 703 | 424
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
July |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2024-07-30 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2024-08-19 | TSS | <2 | 30 | mg/L |  |  |  |  | No
Published | 2024-08-19 | Aluminium | 0.33 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 175 | 878 | 473
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
June |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2024-06-25 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2024-07-04 | TSS | 3 | 30 | mg/L |  |  |  |  | No
Published | 2024-07-09 | Aluminium | 0.62 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 87 | 1581 | 541
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
May |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2024-05-28 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2024-06-08 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2024-07-09 | Aluminium | 0.39 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 87 | 613 | 398
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
April |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2024-04-23 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2024-04-24 | TSS | <2 | 30 | mg/L |  |  |  |  | No
Published | 2024-05-03 | Aluminium | 0.22 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 87 | 607 | 381
Oakey Park Water Treatment Plant
| Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
| March |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
| Sampled | 2024-03-26 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
| Obtained | 2024-03-27 | TSS | 3 | 30 | mg/L |  |  |  |  | No
| Published | 2024-03-05 | Aluminium | 0.21 | n/a | mg/L |  |  |  |  | n/a
|  |  | Daily Flow |  |  | kL/day | 31 | 149 | 458 | 339
Oakey Park Water Treatment Plant
| Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
| February |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
| Sampled | 2024-02-27 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
| Obtained | 2024-02-28 | TSS | <2 | 30 | mg/L |  |  |  |  | No
| Published | 2024-03-11 | Aluminium | 0.22 | n/a | mg/L |  |  |  |  | n/a
|  |  | Daily Flow |  |  | kL/day | 29 | 60 | 375 | 274
Oakey Park Water Treatment Plant
| Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
| January |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
| Sampled | 2024-01-30 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
| Obtained | 2024-01-31 | TSS | 2 | 30 | mg/L |  |  |  |  | No
| Published | 2024-02-07 | Aluminium | 0.28 | n/a | mg/L |  |  |  |  | n/a
|  |  | Daily Flow |  |  | kL/day | 31 | 60 | 388 | 263

## 2023
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
December |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2023-12-19 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2023-12-20 | TSS | 2 | 30 | mg/L |  |  |  |  | No
Published | 2023-12-28 | Aluminium | 0.32 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 59 | 419 | 306
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
November |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2023-11-28 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2023-11-29 | TSS | 14 | 30 | mg/L |  |  |  |  | No
Published | 2023-12-07 | Aluminium | 0.87 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 22 | 517 | 294.2
September |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2023-09-26 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2023-09-27 | TSS | 2 | 30 | mg/L |  |  |  |  | No
Published | 2023-10-26 | Aluminium | 0.31 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 59 | 700 | 299
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
August |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2023-08-29 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2023-09-06 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2023-09-07 | Aluminium | 0.64 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 0 | 359 | 218.8
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
July |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2023-07-26 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2023-08-03 | TSS | 2 | 30 | mg/L |  |  |  |  | No
Published | 2023-08-08 | Aluminium | 0.17 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 61 | 355 | 209
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
June |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2023-06-27 | pH | 7.5 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2023-07-06 | TSS | <2 | 30 | mg/L |  |  |  |  | No
Published | 2023-07-07 | Aluminium | 0.11 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 27 | 118 | 411 | 312
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
May |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2023-05-30 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2023-05-07 | TSS | 6 | 30 | mg/L |  |  |  |  | No
Published | 2023-06-16 | Aluminium | 0.92 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 0 | 496 | 373
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
April |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2023-04-18 | pH | 7.3 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2023-05-01 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2023-05-09 | Aluminium | 0.56 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 0 | 417 | 182
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
March |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2023-03-28 | pH | 7.4 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2023-04-05 | TSS | 5 | 30 | mg/L |  |  |  |  | No
Published | 2023-04-11 | Aluminium | 0.92 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 84 | 665 | 453
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
February |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2023-02-21 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2023-03-03 | TSS | 3 | 30 | mg/L |  |  |  |  | No
Published | 2023-03-10 | Aluminium | 0.35 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 28 | 240 | 742 | 484
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
January |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2023-01-24 | pH | 6.8 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2023-02-01 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2023-02-02 | Aluminium | 0.043 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 0 | 2130 | 613

## 2022
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
December |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-12-20 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-12-30 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2023-01-13 | Aluminium | 0.59 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 0 | 994 | 536
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
November |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-11-29 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-12-09 | TSS | 6 | 30 | mg/L |  |  |  |  | No
Published | 2023-01-13 | Aluminium | 0.62 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 0 | 995 | 228
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
October |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-10-25 | pH | 6.9 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-11-06 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2022-11-14 | Aluminium | 0.63 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 23 | 0 | 901 | 385
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
September |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-09-27 | pH | 6.8 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-10-09 | TSS | 7 | 30 | mg/L |  |  |  |  | No
Published | 2022-10-13 | Aluminium | 1.21 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 24 | 0 | 2267 | 818
August |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-08-31 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-09-09 | TSS | 3 | 30 | mg/L |  |  |  |  | No
Published | 2022-09-19 | Aluminium | 1.16 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 0 | 2775 | 684
July |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-07-26 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-08-06 | TSS | 3 | 30 | mg/L |  |  |  |  | No
Published | 2022-08-10 | Aluminium | 1.16 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 164 | 1280 | 657
June |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-06-28 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-07-09 | TSS | 2 | 30 | mg/L |  |  |  |  | No
Published | 2022-07-15 | Aluminium | 0.5 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 164 | 1280 | 657
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
May |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-05-24 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-06-03 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2022-06-15 | Aluminium | 0.33 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 492 | 1185 | 842
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
April |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-04-26 | pH | 6.9 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-04-27 | TSS | 3 | 30 | mg/L |  |  |  |  | No
Published | 2022-05-11 | Aluminium | 0.47 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 11 | 204 | 994 | 650
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
March |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-03-29 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-04-08 | TSS | 5 | 30 | mg/L |  |  |  |  | No
Published | 2022-04-11 | Aluminium | 0.57 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 2978 | 2978 | 2978
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
February |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-02-22 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-03-03 | TSS | 7 | 30 | mg/L |  |  |  |  | No
Published | 2022-03-07 | Aluminium | 0.68 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 28 | 90 | 1542 | 494
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
January |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2022-01-25 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2022-02-03 | TSS | 6 | 30 | mg/L |  |  |  |  | No
Published | 2022-02-07 | Aluminium | 0.85 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 50 | 728 | 310

## 2021
Oakey Park Water Treatment Plant
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
December |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-12-21 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-12-31 | TSS | 6 | 30 | mg/L |  |  |  |  | No
Published | 2022-01-18 | Aluminium | 0.85 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 0 | 579 | 273
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
November |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-11-23 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-12-08 | TSS | 3 | 30 | mg/L |  |  |  |  | No
Published | 2021-12-09 | Aluminium | 0.35 | n/a | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 0 | 626 | 329
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
October |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-10-26 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-11-06 | TSS | 2 | 30 | mg/L |  |  |  |  | No
Published | 2021-11-10 | Aluminium | 0.17 |  | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 117 | 896 | 574
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
September |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-09-28 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-10-07 | TSS | 2 | 30 | mg/L |  |  |  |  | No
Published | 2021-10-07 | Aluminium | 0.41 |  | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 148 | 864 | 391
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
August |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-08-31 | pH | 7.3 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-09-10 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2021-09-13 | Aluminium | 0.59 |  | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 162 | 907 | 524
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
July |  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-07-27 | pH | 7.3 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-08-06 | TSS | 5 | 30 | mg/L |  |  |  |  | No
Published | 2021-08-10 | Aluminium | 0.78 |  | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 79 | 500 | 302
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-06-29 | pH | 7.7 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-07-10 | TSS | 8 | 30 | mg/L |  |  |  |  | No
Published | 2021-07-13 | Aluminium | 1.61 |  | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 10* | 188 | 1841 | 463
*Note: Previous sampling point 3 has been renamed as Point 1 in the EPA license 2396.
*Note: Only 10 data for this month as plant was offline for maintenance and restarted on 21/06/2021.
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-05-25 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-06-03 | TSS | 6 | 30 | mg/L |  |  |  |  | No
Published | 2021-06-04 | Aluminium | 0.62 |  | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 17* | 100 | 543 | 307
*Note: Previous sampling point 3 has been renamed as Point 1 in the EPA license 2396.
*Note: Only 17 data for this month as plant is offline for maintenance
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-04-27 | pH | 6.8 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-05-26 | TSS | 11 | 30 | mg/L |  |  |  |  | No
Published | 2021-05-27 | Aluminium | 1.01 |  | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 30 | 196 | 812 | 526
*Note: Previous sampling point 3 has been renamed as Point 1 in the EPA license 2396.
Sampling point: 1 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-03-30 | pH | 7.7 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-04-10 | TSS | 3 | 30 | mg/L |  |  |  |  | No
Published | 2021-04-15 | Aluminium | 0.51 |  | mg/L |  |  |  |  | n/a
|  | Daily Flow |  |  | kL/day | 31 | 102 | 641 | 433
*Note: Previous sampling point 3 has been renamed as Point 1 in the EPA license 2396.
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-02-23 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-03-11 | TSS | 35 | 30 | mg/L |  |  |  |  | Yes - During the past 12 months, issues with the water reticulation supply to the outlying villages, have caused a heavy demand on Oakey Park WFP. This extra demand has resulted in excessive sludge build up in the sludge lagoons associated with the plant. Over utilisation of the plant, has also led to a chemical dosing system failure in late February 2021. The combination of this systems failure and excessive sludge from the plant, has resulted in an elevated level of Total Suspended Solids (TSS), when sampled at the end of February 2021. A contractor has been engaged by Council to remove sludge from the lagoons. This should start by the end of March 2021.
Published | 2021-03-17 | Aluminium | 4.44 |  | mg/L
|  | Daily Flow |  |  | kL/day | 28 | 0 | 845 | 320
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2021-01-27 | pH | 6.8 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-02-10 | TSS | 7 | 30 | mg/L |  |  |  |  | No
Published | 2021-02-22 | Aluminium | 0.68 |  | mg/L
|  | Daily Flow |  |  | kL/day | 17** | 58 | 658 | 214
** 14 days during January not recorded due to lightning strike on plant. Repairs completed 14 Jan 2021

## 2020
Oakey Park Water Treatment Plant
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-12-16 | pH | 6.8 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2021-01-11 | TSS | 25 | 30 | mg/L |  |  |  |  | No
Published | 2021-01-18 | Aluminium | 5.49 |  | mg/L
|  | Daily Flow |  |  | kL/day | 23 | 41 | 674 | 308
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-11-24 | pH | 6.5 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-12-14 | TSS | 9 | 30 | mg/L |  |  |  |  | No
Published | 2020-12-22 | Aluminium | 1.84 |  | mg/L
|  | Daily Flow |  |  | kL/day | 14** | 107 | 618 | 382
** 16 days during November not recorded due to lightning strike on plant.
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-10-27 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-11-06 | TSS | 6 | 30 | mg/L |  |  |  |  | No
Published | 2020-11-17 | Aluminium | 0.74 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 57 | 491 | 256
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-09-29 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-10-08 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2020-10-13 | Aluminium | 0.62 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 124 | 340 | 212
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-08-25 | pH | 6.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-09-04 | TSS | 6 | 30 | mg/L |  |  |  |  | No
Published | 2020-09-09 | Aluminium | 0.86 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 42 | 966 | 236
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-07-29 | pH | 6.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-08-11 | TSS | 5 | 30 | mg/L |  |  |  |  | No
Published | 2020-08-12 | Aluminium | 2.77 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 43 | 735 | 216
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-06-23 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-07-16 | TSS | 2 | 30 | mg/L |  |  |  |  | No
Published | 2020-07-16 | Aluminium | 0.32 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 0 | 308 | 186
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-05-27 | pH | 7.5 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-06-04 | TSS | 4 | 30 | mg/L |  |  |  |  | No
Published | 2020-06-11 | Aluminium | 0.66 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 5 | 1165 | 263
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-04-28 | pH | 7.5 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-05-06 | TSS | 3 | 30 | mg/L |  |  |  |  | No
Published | 2020-05-19 | Aluminium | 0.38 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 0 | 291 | 188
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-03-25 | pH | 7.3 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-04-03 | TSS | 11 | 30 | mg/L |  |  |  |  | No
Published | 2020-04-17 | Aluminium | 0.92 |  | mg/L
|  | Daily Flow |  |  | kL/day | 27 | 37 | 415 | 197
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-02-26 | pH | 7.4 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-03-06 | TSS | 8 | 30 | mg/L |  |  |  |  | No
Published | 2020-03-19 | Aluminium | 2.7 |  | mg/L
|  | Daily Flow |  |  | kL/day | 16 | 42 | 378 | 182
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2020-01-29 | pH | 7.3 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-02-12 | TSS | <2 | 30 | mg/L |  |  |  |  | No
Published | 2020-02-25 | Aluminium | 0.25 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 38 | 488 | 233

## 2019
Oakey Park Water Treatment Plant
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-12-18 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2020-01-06 | TSS | 22 | 30 | mg/L |  |  |  |  | No
Published | 2020-01-08 | Aluminium | 3.16 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 82 | 557 | 240
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-11-27 | pH | 6.8 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2019-12-04 | TSS | 5 | 30 | mg/L |  |  |  |  | No
Published | 2019-12-09 | Aluminium | 0.61 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 124 | 444 | 240
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-10-29 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2019-11-12 | TSS | 21 | 30 | mg/L |  |  |  |  | No
Published | 2019-11-13 | Aluminium | 1.26 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 42 | 326 | 228
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-09-25 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
Obtained | 2019-10-03 | TSS | 6 | 30 | mg/L |  |  |  |  | No
Published | 2019-10-21 | Aluminium | 0.98 |  | mg/L
|  | Daily Flow |  |  | kL/day | 8 | 104 | 289 | 197
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-08-28 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2019-09-06 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2019-09-11 | pH | 6.9 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 3 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.56 |  | mg/L
|  | Daily Flow |  |  | kL/day | 23 | 163 | 429 | 244
Sampling point: 5
|  | Oil & Grease | <5
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-07-31 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2019-08-07 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2019-08-13 | pH | 6.9 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 3 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.66 |  | mg/L
|  | Daily Flow |  |  | kL/day | 8 | 120 | 905 | 290
Sampling point: 5
|  | Oil & Grease | <5
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-06-26 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2019-07-16 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2019-07-23 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 5 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.6 |  | mg/L
|  | Daily Flow |  |  | kL/day | 7 | 11 | 890 | 313
Sampling point: 5
|  | Oil & Grease | <5
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-05-29 | BOD | 2 | 10 | mg/L |  |  |  |  | No
Obtained | 2019-06-08 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2019-06-17 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 37 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 3.38 |  | mg/L
|  | Daily Flow |  |  | kL/day | 17 | 16 | 348 | 234
Sampling point: 5
|  | Oil & Grease | <5
Correction Log - Aluminium results not previously recorded, previous reports amended with results.
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-04-23 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2019-05-06 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2019-05-14 | pH | 6.8 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 3 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.43
|  | Daily Flow |  |  | kL/day | 30 | 125 | 389 | 251
Sampling point: 5
|  | Oil & Grease | <5
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-03-26 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2019-04-08 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2019-04-15 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 21 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 1.07
|  | Daily Flow |  |  | kL/day | 29 | 105 | 795 | 277
Sampling point: 5
|  | Oil & Grease | <5
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-02-26 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2019-03-08 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2019-03-14 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 6 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.45
|  | Daily Flow |  |  | kL/day | 28 | 84 | 522 | 270
Sampling point: 5
|  | Oil & Grease | <5
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2019-01-29 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2019-02-06 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2019-02-07 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 10 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.38
|  | Daily Flow |  |  | kL/day | 31 | 126 | 483 | 246
Sampling point: 5
|  | Oil & Grease | <5
Correction Log for January 2019 - values for discharge from Point 3 incorrectly provided as part of the original upload, correction to the data was made 14/03/19

## 2018
Oakey Park Water Treatment Plant
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-12-18 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2019-01-05 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2019-01-10 | pH | 6.4 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 15 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 2.52 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 40 | 1268 | 362
Sampling point: 5
|  | Oil & Grease | <5
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-11-27 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-12-06 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-12-07 | pH | 6.8 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 8 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.78 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 80 | 337 | 234
Sampling point: 5
|  | Oil & Grease | <5
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-10-30 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-11-10 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-11-13 | pH | 6.8 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 5 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.48 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 125 | 265 | 221
Sampling point: 5
|  | Oil & Grease | <5
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-09-25 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-10-03 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-10-08 | pH | 6.5 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 6 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.71 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 115 | 380 | 232
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-08-28 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-09-06 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-09-07 | pH | 6.6 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 9 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.64 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 83 | 422 | 233
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-07-24 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-08-01 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-08-15 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 3 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.63 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 156 | 678 | 343
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-06-26 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-07-04 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-07-09 | pH | 6.8 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 6 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.91 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 82 | 285 | 184
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-05-29 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-06-07 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-06-13 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 4 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.36 |  | mg/L
|  | Daily Flow |  |  | kL/day | 28 | 40 | 245 | 146
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-04-17 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-04-27 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-05-16 | pH | 6.9 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 4 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.65 |  | mg/L
|  | Daily Flow |  |  | kL/day | 20 | 42 | 411 | 170
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-03-28 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-04-07 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-04-13 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 3 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.38 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 83 | 295 | 169
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-02-27 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-03-10 | Oil & Grease | 6 | 10 | mg/L |  |  |  |  | No
Published | 2018-03-16 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 6 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.63 |  | mg/L
|  | Daily Flow |  |  | kL/day | 28 | 86 | 529 | 193
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2018-01-30 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2018-02-08 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-02-16 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 4 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.45 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 41 | 310 | 159

## 2017
Oakey Park Water Treatment Plant
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-12-20 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-12-30 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2018-01-11 | pH | 6.9 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 4 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.54 |  | mg/L
|  | Daily Flow |  |  | kL/day | 27 | 83 | 7102 | 449 | The result of 7,102KL was due to a lightning strike taking power out of the interface
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-11-28 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-12-12 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-12-15 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 2 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.37 |  | mg/L
|  | Daily Flow |  |  | kL/day | 29 | 41 | 276 | 127
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-10-24 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-11-04 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-11-07 | pH | 7.6 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 25 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 8.34 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 82 | 254 | 183
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-09-27 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-10-06 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-10-10 | pH | 7.1 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 2 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.46 |  | mg/L
|  | Daily Flow |  |  | kL/day | 29 | 21 | 489 | 216
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-08-29 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-09-11 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-09-12 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 9 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 1.83 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 84 | 469 | 217
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-07-26 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-08-04 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-08-14 | pH | 6.8 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 8 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.37 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 42 | 962 | 214
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-06-27 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-07-05 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-07-10 | pH | 7.64 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | <5 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.61 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 82 | 300 | 200
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-05-24 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-05-30 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-06-09 | pH | 6.72 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 18 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 1.52 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 119 | 352 | 198
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-04-18 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-04-27 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-05-08 | pH | 6.17 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 15 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 1.16 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 121 | 375 | 216
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-03-22 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-03-30 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-04-07 | pH | 7.2 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 30 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 1.1 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 83 | 351 | 215
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-02-21 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-03-07 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-03-14 | pH | 7.9 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | <5 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.57 |  | mg/L
|  | Daily Flow |  |  | kL/day | 24 | 82 | 652 | 247
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2017-01-18 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-01-31 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-02-14 | pH | 6.62 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | <5 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.37 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 79 | 494 | 255

## 2016
Oakey Park Water Treatment Plant
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-12-20 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2017-01-03 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2017-01-16 | pH | 7.36 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | <5 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.45 |  | mg/L
|  | Daily Flow |  |  | kL/day | 28 | 82 | 380 | 230
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-11-15 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-11-23 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-12-15 | pH | 6.76 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 6 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.51 |  | mg/L
|  | Daily Flow |  |  | kL/day | 22 | 43 | 1085 | 279
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-10-18 | BOD | 3 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-11-01 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-11-11 | pH | 7.32 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | <5 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.68 |  | mg/L
|  | Daily Flow |  |  | kL/day | 29 | 41 | 404 | 134
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-09-20 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-10-20 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-11-01 | pH | 6.9 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | <5 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.09 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 37 | 1585 | 235
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-08-23 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-08-31 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-09-12 | pH | 6.3 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | <5 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.14 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 75 | 277 | 155
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-07-26 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-08-03 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-08-12 | pH | 6.6 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | <5 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.19 |  | mg/L
|  | Daily Flow |  |  | kL/day | 25 | 20 | 467 | 167
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-06-28 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-07-09 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-07-21 | pH | 6.6 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 18 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 1.56 |  | mg/L
|  | Daily Flow |  |  | kL/day | 27 | 47 | 1019 | 184
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-05-24 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-06-06 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-06-14 | pH | 6.3 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 14 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.91 |  | mg/L
|  | Daily Flow |  |  | kL/day | 31 | 28 | 297 | 133
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-04-26 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-05-06 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-05-10 | pH | 6.6 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 2 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.21 |  | mg/L
|  | Daily Flow |  |  | kL/day | 30 | 49 | 248 | 142
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-03-29 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-04-13 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-04-21 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | 2 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.18 |  | mg/L
|  | Daily Flow |  |  | kL/day | 27 | 49 | 670 | 179
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-02-23 | BOD | <2 | 10 | mg/L |  |  |  |  | No
Obtained | 2016-03-16 | Oil & Grease | <5 | 10 | mg/L |  |  |  |  | No
Published | 2016-03-22 | pH | 7 | 6.0 - 8.0 | [5 empty] | No
|  | TSS | <2 | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.14 |  | mg/L
|  | Daily Flow |  |  | kL/day | 21 | 38 | 344 | 174
Sampling point: 3 |  |  | EPL no. 2396 |  |  | Licensee: Lithgow City Council
|  | Quantity | Measurement | Limit | Units | Data Collected | Lowest value | Highest value | Mean | Exceedence
Sampled | 2016-01-19 | BOD |  | 10 | mg/L |  |  |  |  | No
Obtained | 2016-02-01 | Oil & Grease |  | 10 | mg/L |  |  |  |  | No
Published | 2016-02-05 | pH |  | 6.0 - 8.0 | [5 empty] | No
|  | TSS |  | 50 | mg/L |  |  |  |  | No
|  | Aluminium | 0.26 |  | mg/L
|  | Daily Flow |  |  | kL/day | 17 | 1 | 473 | 217